## 2 Parallel RDD
R11 - SCRTST resistor power calculation
SCR_TST is clamped to 20V during positive cycle and is half-wave rectified
| R11 (Ω) | 68000
|  | Pk | RMS | Pk | RMS
| Line | 169.7056 | 120 | 367.6955 | 260
| P | 0.32958 | 0.11653 | 1.7778 | 0.62856
| RDD power calculation (R1, R2, R3, R4) |  |  | RDD (Ω) | 18000
|  | Peak | RMS | Peak | RMS |  | VZ?
| Line | 169.9885 | 120.2 | 367.6955 | 260 |  | 0
| Normal | Peak | RMS | Peak | RMS
| R1¦¦R2 | 9000 | - | 9000 | -
| R3¦¦R4 | 9000 | - | 9000 | -
| IDD | 0.0082994 | 0.0058685 | 0.019283 | 0.013635
| V34 | 74.6942 | 52.8168 | 173.5478 | 122.7168
| V12 | 74.6942 | 52.8168 | 173.5478 | 122.7168
| P12 | 0.61991 | 0.30996 | 3.3465 | 1.6733
| P34 | 0.61991 | 0.30996 | 3.3465 | 1.6733
| P1 - P4 | 0.30996 | 0.15498 | 1.6733 | 0.83663
FAILURE CONDITIONS (open in circuit limiter)
UL 943 Requirement
| One open | Peak | RMS | Peak | RMS
R2 open | R1¦¦R2 = R1 | 18000 | - | 18000 | -
| R3¦¦R4 | 9000 | - | 9000 | -
| IDD | 0.0055329 | 0.0039124 | 0.012855 | 0.0090901
| V34 | 49.7962 | 35.2112 | 115.6985 | 81.8112
| V12=V1 | 99.5923 | 70.4224 | 231.397 | 163.6224
| P12= P1 | 0.55103 | 0.27552 | 2.9747 | 1.4873 | <--limiting factor!
| P34 | 0.27552 | 0.13776 | 1.4873 | 0.74367
R12 - PH resistor power calculation
| R12 (Ω) | 2000000
|  | Pk | RMS | Pk | RMS
| Line | 169.7056 | 120 | 195.1615 | 138 |  | Worst-case power is during negative cycle when PH=GND.
| P | 0.0144 | 0.010182 | 0.019044 | 0.013466 |  | During positive cycle, the PH pin is clamped to VDD=20V rail.
R8 - Q1 collector resistor power calculation
| R8 (Ω) | 10000
|  | Pk | RMS | Pk | RMS
| Line | 169.7056 | 120 | 195.1615 | 138
| Vdrop | 168.9056 | 15.3365 | 194.3615 | 17.637 |  | Worst-case RMS Vdrop scenario is Q1 on for one half-cycle every second for five seconds
| P | 2.8529 | 0.023521 | 3.7776 | 0.031106 |  | Check
[7 empty] | 0.019436 | 0.0017565
17.5647
0.030852
Note on I11: Iliya, Peter: You can slightly reduce power needed with RDD resistors by placing a max 30-V Zener can be with R3¦¦R4.

## 3 Parallel RDD
R11 - SCRTST resistor power calculation
SCR_TST is clamped to 20V during positive cycle and is half-wave rectified
| R11 (Ω) | 68000 | Datasheet to be updated to show 68kΩ
|  | Pk | RMS | Pk | RMS
| Line | 169.7056 | 120 | 367.6955 | 260
| P | 0.32958 | 0.11653 | 1.7778 | 0.62856
| RDD power calculation (R1, R2, R13; R3, R4, R14) |  |  | RDD (Ω) | 24000
|  | Peak | RMS | Peak | RMS |  | VZ?
| Line | 169.7056 | 120 | 367.6955 | 260 |  | 0
| Normal | Peak | RMS | Peak | RMS
| R1¦¦R2¦¦R13 | 8000 | - | 8000 | -
| R3¦¦R4¦¦R14 | 8000 | - | 8000 | -
| IDD | 0.0093191 | 0.0065896 | 0.021693 | 0.01534
| V3_4_14 | 74.5528 | 52.7168 | 173.5478 | 122.7168
| V1_2_13 | 74.5528 | 52.7168 | 173.5478 | 122.7168
| P1213 | 0.69477 | 0.34738 | 3.7649 | 1.8824
| P3414 | 0.69477 | 0.34738 | 3.7649 | 1.8824
| P1 - P4 | 0.23159 | 0.11579 | 1.255 | 0.62748
FAILURE CONDITIONS (open in circuit limiter)
UL 943 Requirement
| One open | Peak | RMS | Peak | RMS
R2 open | R1¦¦R2¦¦13 = R1¦¦R13 | 12000 | - | 12000 | -
| R3¦¦R4¦¦R14 | 8000 | - | 8000 | -
| IDD | 0.0074553 | 0.0052717 | 0.017355 | 0.012272
| V3_4_14 | 59.6423 | 42.1734 | 138.8382 | 98.1734
| V1_2_13=V1_13 | 89.4634 | 63.2602 | 208.2573 | 147.2602
| P1_13 | 0.66697 | 0.33349 | 3.6143 | 1.8071
| P1 = P13 | 0.33349 | 0.16674 | 1.8071 | 0.90356 | <--limiting factor!
| P3_4_14 | 0.44465 | 0.22232 | 2.4095 | 1.2048
R12 - PH resistor power calculation
| R12 (Ω) | 1000000
|  | Pk | RMS | Pk | RMS
| Line | 169.7056 | 120 | 367.6955 | 260
| P | 0.0288 | 0.020365 | 0.1352 | 0.095601
R8 - Q1 collector resistor power calculation
| R8 (Ω) | 10000
|  | Pk | RMS | Pk | RMS
| Line | 169.7056 | 120 | 367.6955 | 260
| Vdrop | 168.9056 | 15.3365 | 366.8955 | 33.2292 |  | Worst-case RMS Vdrop scenario is Q1 on for one half-cycle every second for five seconds
| P | 2.8529 | 0.023521 | 13.4612 | 0.11042 |  | Check
[7 empty] | 0.03669 | 0.0033157
33.1569
0.10994
Note on I11: Iliya, Peter: You can slightly reduce power needed with RDD resistors by placing a max 30-V Zener can be with R3¦¦R4.

## Typcial BOM
Typical Application BOM in datasheet
Notes:
R1, R2, R3, R4 need higher power and/or higher resistance for 260VAC.
R11 max will be updated to 68kΩ in datasheet revision soon to reduce power loss and allow for more options at 260VAC.
R8 resistance can be kept same, but power may need to be increased for 260VAC.
Updates to the Typical BOM for datasheet
R9 | >5kΩ | The datasheet shows 1.5kΩ because that was used during validation, but it requires excess current from VDD during ALARM blinking for many LEDs
C3 | 620nF | This is typical recommended value to keep device from falsely tripping in REJECT zone of the Dalziel Let-go curve. This value should be validated with basic check due transformer impedance variation.
Rs | 500-Ω | A snubber (Rs + Cs) on the output of sensing amplifier has been shown to complelely reduce the chance of a false trip on power up. This false trip occurs during a specific phase of line, which makes internal REF regulator overshoot during power up.
Cs | 10nF