## Instructions
`
© 2023
| Inrush FET SOA Margin Design Calculator- Rev. B |  | `
Typical design procedure
Typical applications require multiple passes through the design tool using MOSFET factors such as transient
thermal response and safe operating area curves. Refer to the following application reports for more detail.
The basic design process follows:
1. Enter operating conditions.
2. Select current limit parameters.
2. Enter MOSTFET SOA characteristics
3. Select start up conditions (load and/or soft start). Check whether FET is operating with reasonable margin, within the SOA curve.
If not, try changing start-up conditions (soft start values, timer values), add more FETs in parallel, or switch to FET with better SOA.
5. Enter desired UVLO and OVLO values to get recommended resistor values.
4. Done
Notes
1. This worksheet is designed for use with Microsoft Excel 5.0 or later. Its use is intended to assist power supply designers in their
routine, day-to-day calculations.
2. All worksheets have light green inputs cells, white calculated cells, yellow warning cells and red high-risk cells.
3. Formulas and device constants used in the spreadsheet are locked to prohibit them from accidentally being overwritten or deleted.
TEXAS INSTRUMENTS TEXT FILE LICENSE Copyright (c) 2023 Texas Instruments Incorporated All rights reserved not granted herein. Limited License. Texas Instruments Incorporated grants a world-wide, royalty-free, non-exclusive license under copyrights and patents it now or hereafter owns or controls to make, have made, use, import, offer to sell and sell ("Utilize") this software subject to the terms herein. With respect to the foregoing patent license, such license is granted solely to the extent that any such patent is necessary to Utilize the software alone. The patent license shall not apply to any combinations which include this software, other than combinations with devices manufactured by or for TI (“TI Devices”). No hardware patent is licensed hereunder. Redistributions must preserve existing copyright notices and reproduce this license (including the above copyright notice and the disclaimer and (if applicable) source code license limitations below) in the documentation and/or other materials provided with the distribution Redistribution and use in binary form, without modification, are permitted provided that the following conditions are met: * No reverse engineering, decompilation, or disassembly of this software is permitted with respect to any software provided in binary form. * any redistribution and use are licensed by TI for use only with TI Devices. * Nothing shall obligate TI to provide you with source code for the software licensed and provided to you in object code. If software source code is provided to you, modification and redistribution of the source code are permitted provided that the following conditions are met: * any redistribution and use of the source code, including any resulting derivative works, are licensed by TI for use only with TI Devices. * any redistribution and use of any object code compiled from the source code and any resulting derivative works, are licensed by TI for use only with TI Devices. Neither the name of Texas Instruments Incorporated nor the names of its suppliers may be used to endorse or promote products derived from this software without specific prior written permission. DISCLAIMER. THIS SOFTWARE IS PROVIDED BY TI AND TI’S LICENSORS "AS IS" AND ANY EXPRESS OR IMPLIED WARRANTIES, INCLUDING, BUT NOT LIMITED TO, THE IMPLIED WARRANTIES OF MERCHANTABILITY AND FITNESS FOR A PARTICULAR PURPOSE ARE DISCLAIMED. IN NO EVENT SHALL TI AND TI’S LICENSORS BE LIABLE FOR ANY DIRECT, INDIRECT, INCIDENTAL, SPECIAL, EXEMPLARY, OR CONSEQUENTIAL DAMAGES (INCLUDING, BUT NOT LIMITED TO, PROCUREMENT OF SUBSTITUTE GOODS OR SERVICES; LOSS OF USE, DATA, OR PROFITS; OR BUSINESS INTERRUPTION) HOWEVER CAUSED AND ON ANY THEORY OF LIABILITY, WHETHER IN CONTRACT, STRICT LIABILITY, OR TORT (INCLUDING NEGLIGENCE OR OTHERWISE) ARISING IN ANY WAY OUT OF THE USE OF THIS SOFTWARE, EVEN IF ADVISED OF THE POSSIBILITY OF SUCH DAMAGE.

## Design Calculator
Mosfet SOA Margin Calculator during dvdt/Inrush limit Startup
Enter Values in Green Shaded Cells
Calculated/Suggested Values are shown in White Cells
Yellow and Red cells highlight pottential issues with the design. Red highlights items that are higher risk.
| Step 1: Operating Conditions |  |  | Minimum Input DC Operating Voltage: VIN(MIN) | 40 | V | Device | GATE Source Current | Units
|  |  |  | Nominal Input DC Operating Voltage: VIN(NOM) | 50 | V | LM74502-Q1 | 60 | µA
|  |  |  | Maximum Input DC Operating Voltage: VIN(MAX) | 55 | V | LM7480x-Q1 | 55 | µA
|  |  |  | Maximum Load Current: IOUT(MAX) | 50 | A | LM7472x-Q1 | 50 | µA
|  |  |  | Maximum Output Load Capacitance: COUT | 2800 | µF | LM749x0-Q1 | 55 | µA
|  |  |  | Maximum Ambient Operating Temperature: TMAX | 55 | oC
|  |  |  | Voltage required at IMON pin at max load, VIMON | 2.7 | V
|  |  |  | Required Overcurrent Timer Duration | 1 | ms
|  |  |  | Required Maximum allowed Inrush Current | 1000 | mA | TPS48xx-Q1, TPS12xx-Q1 | 100 | µA | Pre-charge GATE; Rg = 220Ω
|  |  |  | Typical Current Limit Required | 15 | A
|  |  |  | Required Short circuit current limit | 30 | A
| Steps 1 & 2: Operating Conditions, Current Limit, & Circuit Breaker |  |  | Enter GATE Source Current of the controller | 55 | µA
[7 empty] | TPS48xx-Q1, TPS12xx-Q1 | 75.6 | µA | R1 = 100kΩ; R2 = 10Ω
| Step 2: Current Limit and Circuit Breaker | [9 empty] | Yes
|  |  |  | Enter the Value of Sense Resistor RSNS | 1 | mW |  |  |  |  | No
|  |  |  | Enter value of RSET | 50 | W | [6 empty] | 10 | #DIV/0!
|  |  |  | Suggested value of RILIM | 40 | kW
|  |  |  | Enter RILIM | 40 | kW
|  |  |  | Resulting Minimum Current Limit | 13.5 | A
|  |  |  | Resulting Typical Current Limit | 15 | A
| Steps 1 & 2: Operating Conditions, Current Limit, & Circuit Breaker |  |  | Resulting Maximum Current Limit | 16.5 | A
|  |  |  | Suggested RIMON | 10 | kW | [6 empty] | 100 | #DIV/0!
|  |  |  | Max RIMON | 18.5185 | kW
|  |  |  | Enter RIMON | 10 | kW | [7 empty] | #DIV/0!
|  |  |  | Voltage at IMON pin at max load for above RIMON, VIMON | 2.7 | V
|  |  |  | Suggested Rscp | 1 | kW
|  |  |  | Enter Rscp | 1 | kW
|  |  |  | Resulting Short circuit current limit | 30 | A
|  |  |  | Suggested CTMR | 68 | nF |  |  |  |  | 64.5833
|  |  |  | Selected CTMR | 68 | nF
|  |  |  | Actual Overcurrent Fault Time | 1.0529 | ms
|  |  |  | Auto Retry Time | 1543.6 | ms
| Step 2: MOSFET Selection |  |  | FET driven by GATE | SM1A14NHLD
|  |  |  | Estimated MOSFET RQJA | 40 | oC/W |  |  |  |  | 44.0771 | 3
|  |  |  | Number of MosFETs in parallel driven by HGATE | 2 | # |  |  |  |  | Values Used
|  |  |  | MOSFET On resistance @ TJ,DC | 1.9 | mW |  |  |  |  | 1.9
|  |  |  | Maximum FET Junction Temperature | 175 | oC |  |  |  |  | 175
|  |  |  | 100ms SOA Current (re-use 1ms data if unavailable) @ VIN(MAX) | 100 | A |  |  |  |  | 100
|  |  |  | 1ms SOA Current @ VIN(MAX) | 8 | A |  |  |  |  | 8
|  |  |  | 10ms SOA Current @ VIN(MAX) | 2 | A |  |  |  |  | 2
|  |  |  | 100ms Current at @ VIN(MAX) (use DC if 100ms not available) | 2 | A |  |  |  |  | 2
| Step 2: MOSFET Selection |  |  | 1s or DC SOA Current at @ VIN(MAX) (use DC if 1s not available) | 2 | A |  |  |  |  | 2
| Note: TI recommends choosing a FET with SOA current specified for 100ms and/or 1s or DC. If choosing a FET without these parameters, this calculator will estimate the values via extrapolation, which leaves an inherent associated risk. |  |  | FET Power dissapation at full load (per FET) | 1.1875 | W
|  |  |  | Maximum steady state FET Junction Temperature (TJ,DC) | 102.5 | oC
Note: Hover here to see the 3 values affecting this curve, consult a thermal expert if you are unsure!
| Step 3: Startup FET SOA Margin calculations |  |  | Load Turn-On Threshold | 6 | V
|  |  |  | Startup Load Type | Resistive
|  |  |  | Startup Load Value | 3 | Ohms |  |  |  |  | Constant Current
|  |  |  | Use External Soft-Start Control | Yes | [5 empty] | Resistive
|  |  |  | Enter Crss of Q2 FET/s Driven by HGATE | 0.5 | nF
|  |  |  | Calculated SS capacitance Cdv/dt | 154 | nF
|  |  |  | Select SS capacitance Cdv/dt | 22 | nF
|  |  |  | dv/dt rate on Vout for above capacitor | 2.5 | V/ms
|  |  |  | Actual Inrush Current | 7 | A
| Step 3: Startup |  |  | SOA margin during start-up | 0.18283
|  |  |  | Start-up time | 22 | ms
| Step 5: UVLO, OVLO & PGD Thresholds |  |  | Select Option A or Option B | Option B | [5 empty] | Option A
|  |  |  | Desired UVLO Threshold | 5 | V |  |  |  |  | Option B
|  |  |  | Desired OVLO Threshold | 37 | V
|  |  |  | Recommended Resistance for: R1 | 100 | kW
|  |  |  | R2 | 12.3596 | kW
|  |  |  | R3 | 100 | kW
|  |  |  | R4 | 1.6484 | kW
|  |  |  | Enter the Resistance for R1 | 100 | kW
|  |  |  | Enter the Resistance for R2 | 11.5 | kW
|  |  |  | Enter the Resistance for R3 | 100 | kW
|  |  |  | Enter the Resistance for R4 | 1.65 | kW
Resulting Thresholds:
|  |  |  | Resulting UVLO Falling Threshold = | 5.3326 | V
|  |  | Resulting UVLO Rising Threshold = |  | 5.8174 | V
|  |  | Resulting OVLO Falling Threshold = |  | 33.8833 | V
|  |  |  | Resulting OVLO Rising Threshold = | 36.9636 | V
If any of the above cells is red, see the Instructions Worksheet
| Design Summary |  |  | RSENSE = | 1 | mW
|  |  |  | RSET= | 50 | W
|  |  |  | RSCP= | 1 | kW
|  |  |  | CT = | 68 | nF
|  |  |  | R1 = | 100 | kW
|  |  |  | R2 = | 11.5 | kW
|  |  |  | R3 = | 100 | kW
|  |  |  | R4 = | 1.65 | kW
|  |  |  | RILIM= | 40 | kW
|  |  |  | RIMON= | 10 | kW
|  |  |  | CIN = | 0.01 | µF
|  |  |  | COUT= | 2800 | µF
|  |  |  | Cdv/dt = | 22 | nF
|  |  |  | Q1 = | SM1A14NHLD
|  |  |  | Q2 = | SM1A14NHLD
|  |  |  | Z1 = | SMBJ33CA
| Notes: | 1. Although not mandatory, CIN provides transient suppression at the VIN pin
2. A TVS clamp from VIN to GND is absolutely mandatory to clamp the voltage overshoot upon MOSFET turn-off, e.g. during circuit breaker
3. Component tolerances not accounted for in Min/Max Calculations.
Note on F18: This is the capacitance at Vout. This should not be zero. A minimum of 100 nF is recommended.
Note on F23: Min current limit has to be greater than max load current
Note on F24: Value depends on Rsense, should not be less than 20mV/Rsense
Note on F25: Refer to controller datasheet for Load switch FET - 'GATE Source Current' paramter
Note on F30: Recommended range is 50 to 100 ohm
Note on F33: Ensure that the minimum current limit is above maximum load.
Note on F49: Note that this parameter is heavily dependent on the board layout and amount of copper connected to the Drain of the FET. ~40 C/W number and is a good starting point. It's recommended to measure this value again once the boards are built and plugging this back into the calculator.
Note on F51: This number may need to be adjusted iteratively.
Note on F59: If FET temperature is too high, increase the # of FETs, reduce the load, or reduce the RθJA by adding more heat sinking to MOSFETs.
Note on I65: 3 Parameters: Step 1: Max Ambrient Operating Temperature Step 3: Estimated MOSFET RQJA Step 3: FET Power Dissipation at full load **This includes air flow
Note on F67: Select if the load will draw current during start-up. For no Load, choose constant current and set to zero
Note on F69: Yes or No. DV/DT control can be useful in high current applications or applications were COUT is large.
Note on F74: Should be less than the user specified Inrush current value, vary the slew rate and SS Capacitor to get it below max value
Note on F75: A margin of >1.1 is required and a margin of >1.3 is recommended to account for the variation in the gate current. Reduce dv/dt rate to reduce inrush current and increase SOA margin
Note on F80: See the schematics on the right to select the appropriate option for setting the input voltage UVLO and OVLO thresholds.
Note on F81: This threshold must be between 3V and 65V.
Note on F83: This threshold must be greater than the UVLO Threshold, and less than 65V.
Note on F119: TI recommended. Same as EVM
Note on F120: TI recomends the SMBJxx TVS, which are used on the EVM. Pick the proper value based on the input voltage.
Note: This worksheet provides reasonable understanding on the Mosfet SOA margin while starting up with dvdt control.Tolerances of the components are not included in the calculations. See the Instructions tab for additional information.
Max RS = 45 mV
(Max Load Current x 1.01)
The 1.01 factor provides 1% margin from the max. normal load current.
R2
Z1

## Device Parmaters (hidden)
|  | Min | Typ | Max | Units
Operating Conditions
| Junction Temperature | -40 |  | 125
| Input Voltage | 3 |  | 65 | V
Current Limit
| SCP Threshold RISCP=0 | 18 | 20 | 22 | mV
| SCP Threshold for given RISCP | 27 | 30 | 33 | mV
| Sense input Current |  | 10 |  | uA
Power Limit
| Systematic Offset |  |  | 0.0021 | V
| Minimum Recommended Vsns |  |  | 0.004 | V | <= I am assuming this would have +/- 50% error at best
| A_coeff |  |  | 194000
| Key Equations: | Vsns = Rpwr / (A*Vds) + Vos,syst | [5 empty] | Example: | Vds | Rpwr | Rsns (m-ohm) | Plim | Vsns (mV) | Plim | Rpwr
|  | Plim (Vds) = 1/Rs * [ Rpwr/A + Vds * Vos, syst] | [6 empty] | 12 | 25 | 0.5 | 308.132 | 0.012839 | 82 | 3065.2
|  | Rpwr = A * [PLIM(Vds) * Rs - Vds*Vos,syst] | [6 empty] | 12 | 5 | 0.5 | 101.9464 | 0.0021499
| How Plim varries vs Vds: | [6 empty] | Ex: Plim @ 13V = 100W, Rs = 0.5; Plim @ (Vds = 5V) = 100W - 7V * 1mV/0.5mili-ohm = 100W - 14W = 86W
DELAY TIMER
| TMR source current |  | 79 |  | uA
| TMR sink current |  | 2.5 |  | uA
| Voltage at TMR pin for IWRN shut off |  | 1.2 |  | V
Timer
| Upper Threshold | 1.54 | 1.7 | 1.85 | V
| Insertion Time Current | -3 | -5.5 | -8 | uA
timer_constant
| Fault detection current | 120 | 90 | 60 | uA
| Computed Start - Up Slop |  | 0.74613 |  |  | <= mean root square(T_start_error_Plim, timer_error, cap_error); T_start proportional to 1/Plim => T_start_error_plim = 1/(1-Plim_err) - 1 = 1/(1-0.4) - 1 = 0.66
| Slop for calculations |  | 0.75 |  |  | Note: We get additional buffer, b/c this is designed for a Vinmax, while typically Vin = Vinnom
Gate
| Gate Sourcing Current |  | 55
Circuit Breaker
| 1.8 x Threshold | 35 | 45 | 55
| 1.8x CB:CL Ratio | 1.6 | 1.8 | 2
| 3.6 x Threshold | 70 | 90 | 110
| 3.6x CB:CL Ratio | 3.1 | 3.6 | 4
Timer Pin
| Upper Threshold | 1.54 | 1.7 | 1.85
| Lower Threshold (Restart) | 0.85 | 1 | 1.07
| End of Cycle |  | 0.3
| Re-enable threshold |  | 0.3
| Insertion time current | 3 | 5.5 | 8
| Sink current, end of insertion | 1.4 | 1.9 | 2.4
| Fault detection current | 60 | 90 | 120
| Fault sink current |  | 2.8
Power Good
| PGVOL |  | 25 | 60 | mV | 2 | mA sinking
FB Pin
| FB Threshold | 1.141 | 1.167 | 1.19 | V
| FB Hysteresis Current | 18 | 24 | 31 | uA
OV UV
| UVLOR |  | 0.6 |  | V
| UVLOF |  | 0.55 |  | V
| IUVLO |  | 52 |  | nA
| OVR |  | 0.6 |  | V
| OVF |  | 0.55 |  | V
| IOV |  | 53 |  | nA

## Equations (hidden)
Current Limit
|  |  | CLMIN = | 27 | mV
|  |  | CLNOM = | 30 | mV
|  |  | CLMAX = | 33 | mV
|  |  |  | Max Rs = | 0.54
|  |  |  | RCL1 Recommended = | #REF!
|  |  |  | RCL2 Recommmended = | #REF!
|  |  |  | Effective Rs = | 1 |  | Typ. Current limit = | 15
|  |  |  | Min. Current limit = | 27
|  |  |  | Typ. Current limit = | 30 |  | Actual Current limit= | 62.5
|  |  |  | Max. Current limit = | 33
|  |  |  | Rs Power Diss. = | 1089
|  |  |  | RILIM= | 40
|  |  |  | RIMON= | 10 |  | Actual VIMON= | 2.7 |  | Max RIMON= | 18.5185
|  |  |  | CTMR= | 64.5833 |  | Suggested CTMR= | 68 |  | Selected CTMR= | 68
|  |  |  | Tretry= | 1543.6 |  | OC time= | 1.0529
|  |  |  | RSCP | 1 |  | ISCP= | 30
FET Selection
[5 empty] | Nominal |  | Derated at TJ
|  |  |  | 100ms SOA Current Maximum Input Voltage | 5500 | W | 2658.3333
|  |  |  | 1ms SOA Current Maximum Input Voltage | 440 | W | 212.6667
|  |  |  | 10ms SOA Current Maximum Input Voltage | 110 | W | 53.1667
|  |  |  | 100ms or DC SOA Current at Maximum Input Voltage | 110 | W | 53.1667
|  |  |  | Minimum Power Limit= | 220 | W
|  |  |  | Target PLIM | 0 | W
|  |  |  | Rpwr | -22.407 | k-ohm
|  |  |  | Rpwr actual | 0 | k-ohm
|  |  |  | Final Plim | 115.5 | W
|  |  |  | Resulting Typical Power Limit = | 87.78 | 24% tolerance used in this calculation.
|  |  |  | Resulting Minimum Power Limit = | 115.5
|  |  |  | Resulting Maximum Power Limit = | 143.22
Startup
With PLIM
|  |  |  | Typical Start time | 22 | ms
|  |  |  | Start-slop | 0.75
|  |  |  | Target Fault Timer | 38.5 | ms
|  |  |  | Target Timer capacitance | 2038.2353 | nF
|  |  |  | Selected Timer capacitance | #REF! | nF
|  |  |  | Final Fault Timer | #REF! | ms
|  |  |  | SOA / PLIM | #REF!
|  |  |  | Inrush Duration | 140 | ms
With SS
|  |  |  | Inrush Current | 1000 | mA
|  |  |  | dv/dt rate | #REF! | V/ms
|  |  |  | calculated SS capacitance | 154 | nF
|  |  |  | actual SS capacitance | 22 | nF
|  |  |  | actual dv/dt rate | 2.5 | V/ms | #REF!
|  |  |  | I_Cout | 7 | A
|  |  |  | typical start time | 22 | ms
|  |  |  | FET Energy dissipated at start-up (EFET) | 7.7658 | J
|  |  |  | Peak Power dissipated during start-up (PFET) | 481.3314 | W
|  |  |  | Equivalent time at peak power - EFET/PFET (t_power) | 16.1339 | ms
|  |  |  | Available SOA for t_power at Vinmax | 88 | W
|  |  |  | SOA margin | 0.18283
[5 empty] | 1 | ms
Covering hot-short, start-into short for SS
|  |  |  | Target Fault Time | 22
|  |  |  | Calculated Timer Capacitance | 1164.7059 | nF
|  |  |  | Actual Timer Capacitance | #REF! | nF
|  |  |  | Actual Fault Time (Tfault) | #REF! | ms
|  |  |  | Available derated SOA for Tfault | #REF! | W
|  |  |  | SOA margin | #REF!
10% margin added in this calculation
[8 empty] | UVLO upper is F40 |  |  | R1 is F48
A
V/S
nF
|  |  |  | Min Insertion time = | #REF! | ms
|  |  |  | Typ. Insertion time = | #REF! | ms
|  |  |  | Max Insertion time = | #REF! | ms
|  |  |  | Min Restart time = | #REF! | ms | 0.027417 | 1.9714 | 0.19643
|  |  |  | Typ. Restart time = | #REF! | ms | 0.054444 | 2 | 0.25
|  |  |  | Max Restart time = | #REF! | ms | 0.11667 | 2.2286 | 0.275
|  |  |  | Min PG Threshold = | #REF!
|  |  |  | Nom PG Threshold = | #REF!
|  |  |  | Max PG Threshold = | #REF!
|  |  |  | Min PG Hysteresis = | #REF!
|  |  |  | Nom PG Hysteresis = | #REF!
|  |  |  | Max PG Hysteresis = | #REF!
Option A
Option B
[5 empty] | A | B
|  |  |  | R1 = | 94.8991 | 100
|  |  |  | R2 = | 10 | 12.3596
|  |  |  | R3 = | 1.7291 | 100
|  |  |  | R4 = |  | 1.6484
|  |  |  | Resulting UVLO= | 1.0433 | 1.1381 | 5.3326 | 5.8174
|  |  |  | Resulting OVLO= | 1.269 | 1.1633 | 36.9636 | 33.8833
|  |  |  | Ramp time for output voltage | #REF! | ms
|  |  |  | Nominal output voltage | 50 | V
|  |  |  | Required soft-start capacitance | #REF! | nF
GRAPH:
|  |  |  | Selected Rs = | 1
|  |  |  | Selected RPWR = | 0
|  |  |  | Max System voltage = | 55
|  |  |  | Current Lim (min) = | 56.25
|  |  |  | Current Lim (typ) = | 62.5
|  |  |  | Current Lim (max) = | 68.75
|  |  |  | Power Limit (min) = | 87.78
|  |  |  | Power Limit (typ) = | 115.5
|  |  |  | Power Limit (max) = | 143.22
|  |  | A) This table calculates the Ids current based |  |  |  |  | B) This table corrrects the table at left so no |  |  |  | C) This table creates the |  |  | D) This table changes ID values to zero for Vds>Vin(max)
|  |  | on power limit only - no current limit info. |  |  |  |  | current is greater than the current limit. |  |  |  | SOA data points from |  |  | and adds the SOA curve. This data is plotted.
| PLIM |  | Vds | Min | Typ | Max |  | Vds | Min | Typ | Max | the customer's SOA |  |  | Vds | Min | Typ | Max | SOA | Temp Derated SOA
| 115.5 |  | 1 | 86.625 | 115.5 | 144.375 |  | 1 | 56.25 | 62.5 | 68.75 | data he entered. |  |  | 55 | 56.25 | 7 | 68.75 | 1.6 | 88 | W
| 115.5 |  | 2 | 43.3125 | 57.75 | 72.1875 |  | 2 | 43.3125 | 57.75 | 68.75 |  |  |  | 54.4712 | 43.3125 | 7 | 68.75 | 1.6155
| 115.5 |  | 3 | 28.875 | 38.5 | 48.125 |  | 3 | 28.875 | 38.5 | 48.125 |  | User's |  | 53.9423 | 28.875 | 7 | 48.125 | 1.6314
| 115.5 |  | 4 | 21.6562 | 28.875 | 36.0937 |  | 4 | 21.6562 | 28.875 | 36.0937 | Vds | Ids |  | 53.4135 | 21.6562 | 7 | 36.0937 | 1.6475
| 115.5 |  | 5 | 17.325 | 23.1 | 28.875 |  | 5 | 17.325 | 23.1 | 28.875 | 1 | #REF! | x = customer's entry | 52.8846 | 17.325 | 7 | 28.875 | 1.664
| 115.5 |  | 6 | 14.4375 | 19.25 | 24.0625 |  | 6 | 14.4375 | 19.25 | 24.0625 | 2 | #REF! |  | 52.3558 | 14.4375 | 7 | 24.0625 | 1.6808
| 115.5 |  | 7 | 12.375 | 16.5 | 20.625 |  | 7 | 12.375 | 16.5 | 20.625 | 3 | #REF! |  | 51.8269 | 12.375 | 7 | 20.625 | 1.698
| 115.5 |  | 8 | 10.8281 | 14.4375 | 18.0469 |  | 8 | 10.8281 | 14.4375 | 18.0469 | 4 | #REF! |  | 51.2981 | 10.8281 | 7 | 18.0469 | 1.7155
| 115.5 |  | 9 | 9.625 | 12.8333 | 16.0417 |  | 9 | 9.625 | 12.8333 | 16.0417 | 5 | #REF! | x | 50.7692 | 9.625 | 7 | 16.0417 | 1.7333
| 115.5 |  | 10 | 8.6625 | 11.55 | 14.4375 |  | 10 | 8.6625 | 11.55 | 14.4375 | 6 | #REF! |  | 50.2404 | 8.6625 | 7 | 14.4375 | 1.7516
| 115.5 |  | 11 | 7.875 | 10.5 | 13.125 |  | 11 | 7.875 | 10.5 | 13.125 | 7 | #REF! |  | 49.7115 | 7.875 | 7 | 13.125 | 1.7702
| 115.5 |  | 12 | 7.2187 | 9.625 | 12.0312 |  | 12 | 7.2187 | 9.625 | 12.0312 | 8 | #REF! |  | 49.1827 | 7.2187 | 7 | 12.0312 | 1.7892
| 115.5 |  | 13 | 6.6635 | 8.8846 | 11.1058 |  | 13 | 6.6635 | 8.8846 | 11.1058 | 9 | #REF! |  | 48.6538 | 6.6635 | 9.1154 | 11.1058 | 1.8087
| 115.5 |  | 14 | 6.1875 | 8.25 | 10.3125 |  | 14 | 6.1875 | 8.25 | 10.3125 | 10 | #REF! | x | 48.125 | 6.1875 | 9.2917 | 10.3125 | 1.8286
| 115.5 |  | 15 | 5.775 | 7.7 | 9.625 |  | 15 | 5.775 | 7.7 | 9.625 | 11 | #REF! |  | 47.5962 | 5.775 | 9.4679 | 9.625 | 1.8489
| 115.5 |  | 16 | 5.4141 | 7.2187 | 9.0234 |  | 16 | 5.4141 | 7.2187 | 9.0234 | 12 | #REF! |  | 47.0673 | 5.4141 | 9.6442 | 9.0234 | 1.8697
| 115.5 |  | 17 | 5.0956 | 6.7941 | 8.4926 |  | 17 | 5.0956 | 6.7941 | 8.4926 | 13 | #REF! |  | 46.5385 | 5.0956 | 9.8205 | 8.4926 | 1.8909
[12 empty] | 14 | #REF! |  | 46.0096 | 0 | 9.9968 | 0 | 1.9126
|  |  | Note: I added an adjustment for the systematic offset | [8 empty] | 15 | 0 | x | 45.4808 | 0 | 10.1731 | 0 | 1.9349
[12 empty] | 16 | 0 |  | 44.9519 | 0 | 10.3494 | 0 | 1.9576
|  |  | Vos syst | 0 | [7 empty] | 17 | 0 |  | 44.4231 |  | 10.5256 |  | 1.981
|  |  | Rs (ohm) | 0.001 | [7 empty] | 18 | 0 |  | 43.8942 |  | 10.7019 |  | 2.0048
|  |  | Vin, max | 55 | [7 empty] | 19 | 0 |  | 43.3654 |  | 10.8782 |  | 2.0293
|  |  | Plim tolerance |  | 0.25 | [6 empty] | 20 | 0 | x | 42.8365 |  | 11.0545 |  | 2.0543
[15 empty] | 42.3077 |  | 11.2308 |  | 2.08
|  |  | Plim (Vds) = Plim (Vin,max) + (Vds - Vin,max)*Vos,syst/Rs | [11 empty] | 41.7788 |  | 11.4071 |  | 2.1063
[15 empty] | 41.25 |  | 11.5833 |  | 2.1333
[15 empty] | 40.7212 |  | 11.7596 |  | 2.161
[15 empty] | 40.1923 |  | 11.9359 |  | 2.1895
[15 empty] | 39.6635 |  | 12.1122 |  | 2.2187
[15 empty] | 39.1346 |  | 12.2885 |  | 2.2486
[15 empty] | 38.6058 |  | 12.4647 |  | 2.2795
[15 empty] | 38.0769 |  | 12.641 |  | 2.3111
[15 empty] | 37.5481 |  | 12.8173 |  | 2.3437
[15 empty] | 37.0192 |  | 12.9936 |  | 2.3771
[15 empty] | 36.4904 |  | 13.1699 |  | 2.4116
[15 empty] | 35.9615 |  | 13.3462 |  | 2.4471
[15 empty] | 35.4327 |  | 13.5224 |  | 2.4836
[15 empty] | 34.9038 |  | 13.6987 |  | 2.5212
[15 empty] | 34.375 |  | 13.875 |  | 2.56
[15 empty] | 33.8462 |  | 14.0513 |  | 2.6
[15 empty] | 33.3173 |  | 14.2276 |  | 2.6413
[15 empty] | 32.7885 |  | 14.4038 |  | 2.6839
[15 empty] | 32.2596 |  | 14.5801 |  | 2.7279
[15 empty] | 31.7308 |  | 14.7564 |  | 2.7733
[15 empty] | 31.2019 |  | 14.9327 |  | 2.8203
[15 empty] | 30.6731 |  | 15.109 |  | 2.869
[15 empty] | 30.1442 |  | 15.2853 |  | 2.9193
[15 empty] | 29.6154 |  | 15.4615 |  | 2.9714
[15 empty] | 29.0865 |  | 15.6378 |  | 3.0255
[15 empty] | 28.5577 |  | 15.8141 |  | 3.0815
[15 empty] | 28.0288 |  | 15.9904 |  | 3.1396
[15 empty] | 27.5 |  | 16.1667 |  | 3.2
[15 empty] | 26.9712 |  | 16.3429 |  | 3.2627
[15 empty] | 26.4423 |  | 16.5192 |  | 3.328
[15 empty] | 25.9135 |  | 16.6955 |  | 3.3959
[15 empty] | 25.3846 |  | 16.8718 |  | 3.4667
[15 empty] | 24.8558 |  | 17.0481 |  | 3.5404
[15 empty] | 24.3269 |  | 17.2244 |  | 3.6174
[15 empty] | 23.7981 |  | 17.4006 |  | 3.6978
[15 empty] | 23.2692 |  | 17.5769 |  | 3.7818
[15 empty] | 22.7404 |  | 17.7532 |  | 3.8698
[15 empty] | 22.2115 |  | 17.9295 |  | 3.9619
[15 empty] | 21.6827 |  | 18.1058 |  | 4.0585
[15 empty] | 21.1538 |  | 18.2821 |  | 4.16
[15 empty] | 20.625 |  | 18.4583 |  | 4.2667
[15 empty] | 20.0962 |  | 18.6346 |  | 4.3789
[15 empty] | 19.5673 |  | 18.8109 |  | 4.4973
[15 empty] | 19.0385 |  | 18.9872 |  | 4.6222
[15 empty] | 18.5096 |  | 19.1635 |  | 4.7543
[15 empty] | 17.9808 |  | 19.3397 |  | 4.8941
[15 empty] | 17.4519 |  | 19.516 |  | 5.0424
[15 empty] | 16.9231 |  | 19.6923 |  | 5.2
[15 empty] | 16.3942 |  | 19.8686 |  | 5.3677
[15 empty] | 15.8654 |  | 20.0449 |  | 5.5467
[15 empty] | 15.3365 |  | 20.2212 |  | 5.7379
[15 empty] | 14.8077 |  | 20.3974 |  | 5.9429
[15 empty] | 14.2788 |  | 20.5737 |  | 6.163
[15 empty] | 13.75 |  | 20.75 |  | 6.4
[15 empty] | 13.2212 |  | 20.9263 |  | 6.656
[15 empty] | 12.6923 |  | 21.1026 |  | 6.9333
[15 empty] | 12.1635 |  | 21.2788 |  | 7.2348
[15 empty] | 11.6346 |  | 21.4551 |  | 7.5636
[15 empty] | 11.1058 |  | 21.6314 |  | 7.9238
[15 empty] | 10.5769 |  | 21.8077 |  | 8.32
[15 empty] | 10.0481 |  | 21.984 |  | 8.7579
[15 empty] | 9.5192 |  | 22.1603 |  | 9.2444
[15 empty] | 8.9904 |  | 22.3365 |  | 9.7882
[15 empty] | 8.4615 |  | 22.5128 |  | 10.4
[15 empty] | 7.9327 |  | 22.6891 |  | 11.0933
[15 empty] | 7.4038 |  | 22.8654 |  | 11.8857
[15 empty] | 6.875 |  | 23.0417 |  | 12.8
[15 empty] | 6.3462 |  | 23.2179 |  | 13.8667
[15 empty] | 5.8173 |  | 23.3942 |  | 15.1273
[15 empty] | 5.2885 |  | 23.5705 |  | 16.64
[15 empty] | 4.7596 |  | 23.7468 |  | 18.4889
[15 empty] | 4.2308 |  | 23.9231 |  | 20.8
[15 empty] | 3.7019 |  | 24.0994 |  | 23.7714
[15 empty] | 3.1731 |  | 24.2756 |  | 27.7333
[15 empty] | 2.6442 |  | 24.4519 |  | 33.28
[15 empty] | 2.1154 |  | 24.6282 |  | 41.6
[15 empty] | 1.5865 |  | 24.8045 |  | 55.4667
[15 empty] | 1.0577 |  | 24.9808 |  | 83.2
[15 empty] | 0.52885 |  | 25.1571 |  | 166.4
[15 empty] | 0 |  | 25.3333 |  | #DIV/0!
Rpwr = 1.71 x 105 x Rs x PFET
PFET(min) = 4.44 x 10-6 x Rpwr
Rs
PFET(typ) = 5.85 x 10-6 x Rpwr
Rs
PFET(max) = 7.25 x 10-6 x Rpwr
Rs

## Start_up (hidden)
| PLIM | ILIM | Load type |  | SS | Load Value | Load start | Rs | Vos,syst |  |  | Start-time |  | I_fet-I_L margin |  | I_g(hi/nom) | I_g(low/nom)
| 1000000000 | 15 | R |  | Yes | 3 | 6 | 1 | 0.0021 |  |  | 22 | ms | 28.22% |  | 0 | 0
|  |  | To avoid timer running: Iload + Icap,ss < IFET_PLIM / 2 => SS_RATE < 1/Cout * (IFET_PLIM/2 - ILOAD) | [8 empty] | Max_SS_Rate | 51.7262 | V/ms | max_power_typ | 481.3314 | W
[12 empty] | FET_ENERGY | 7.7658 | J | max_power_high | 252.0833 | W
[15 empty] | max_power_low | 252.0833 | W
VIN | Vout | ILOAD |  | IFET_Crss | I_FET_SS | IFET | ICAP | Dt | Time | Tiime (ms) | I_Fet-IL margin | Max _allowed SS_rate | FET_Energy | Power (W) | P_ fast_SS | P_slow_SS
[10 empty] | -10 |  |  |  | 0
[10 empty] | -0.01 |  |  |  | 0
55 | 0 | 0 |  | 308 | 7 | 7 | 7 | 0 | 0 | 0 | 100% | 55 | 0 | 385 | 0 | 0
55 | 0.52885 | 0 |  | 308 | 7 | 7 | 7 | 0.00021154 | 0.00021154 | 0.21154 | 100% | 55 | 0.080659 | 381.2981 | 0 | 0
55 | 1.0577 | 0 |  | 308 | 7 | 7 | 7 | 0.00021154 | 0.00042308 | 0.42308 | 100% | 55 | 0.079876 | 377.5962 | 0 | 0 |  | Start-up slop
55 | 1.5865 | 0 |  | 308 | 7 | 7 | 7 | 0.00021154 | 0.00063462 | 0.63462 | 100% | 55 | 0.079093 | 373.8942 | 0 | 0 |  | QG | 0.3
55 | 2.1154 | 0 |  | 308 | 7 | 7 | 7 | 0.00021154 | 0.00084615 | 0.84615 | 100% | 55 | 0.07831 | 370.1923 | 0 | 0 |  | I_Src | 0.3
55 | 2.6442 | 0 |  | 308 | 7 | 7 | 7 | 0.00021154 | 0.0010577 | 1.0577 | 100% | 55 | 0.077527 | 366.4904 | 0 | 0 |  | RMS | 0.42426
55 | 3.1731 | 0 |  | 308 | 7 | 7 | 7 | 0.00021154 | 0.0012692 | 1.2692 | 100% | 55 | 0.076744 | 362.7885 | 0 | 0
55 | 3.7019 | 0 |  | 308 | 7 | 7 | 7 | 0.00021154 | 0.0014808 | 1.4808 | 100% | 55 | 0.075961 | 359.0865 | 0 | 0 |  | PLIM | 0.3
55 | 4.2308 | 0 |  | 308 | 7 | 7 | 7 | 0.00021154 | 0.0016923 | 1.6923 | 100% | 55 | 0.075178 | 355.3846 | 0 | 0 |  | combined | 0.42426
55 | 4.7596 | 0 |  | 308 | 7 | 7 | 7 | 0.00021154 | 0.0019038 | 1.9038 | 100% | 55 | 0.074394 | 351.6827 | 0 | 0
55 | 5.2885 | 0 |  | 308 | 7 | 7 | 7 | 0.00021154 | 0.0021154 | 2.1154 | 100% | 55 | 0.073611 | 347.9808 | 0 | 0 |  | I_timer | 0.2
55 | 5.8173 | 0 |  | 308 | 7 | 7 | 7 | 0.00021154 | 0.0023269 | 2.3269 | 100% | 55 | 0.072828 | 344.2788 | 0 | 0 |  | C_timer | 0.2
55 | 6.3462 | 2.1154 |  | 310.1154 | 9.1154 | 9.1154 | 7 | 0.00021154 | 0.0025385 | 2.5385 | 76.79% | 54.6223 | 0.093817 | 443.4985 | 102.9216 | 102.9216 |  | RMS | 0.28284
55 | 6.875 | 2.2917 |  | 310.2917 | 9.2917 | 9.2917 | 7 | 0.00021154 | 0.00275 | 2.75 | 75.34% | 54.5908 | 0.094592 | 447.1615 | 110.2865 | 110.2865
55 | 7.4038 | 2.4679 |  | 310.4679 | 9.4679 | 9.4679 | 7 | 0.00021154 | 0.0029615 | 2.9615 | 73.93% | 54.5593 | 0.095327 | 450.6379 | 117.4649 | 117.4649 |  | Final | 0.5099
55 | 7.9327 | 2.6442 |  | 310.6442 | 9.6442 | 9.6442 | 7 | 0.00021154 | 0.0031731 | 3.1731 | 72.58% | 54.5278 | 0.096023 | 453.928 | 124.4568 | 124.4568
55 | 8.4615 | 2.8205 |  | 310.8205 | 9.8205 | 9.8205 | 7 | 0.00021154 | 0.0033846 | 3.3846 | 71.28% | 54.4963 | 0.09668 | 457.0316 | 131.2623 | 131.2623
55 | 8.9904 | 2.9968 |  | 310.9968 | 9.9968 | 9.9968 | 7 | 0.00021154 | 0.0035962 | 3.5962 | 70.02% | 54.4649 | 0.097297 | 459.9487 | 137.8814 | 137.8814
55 | 9.5192 | 3.1731 |  | 311.1731 | 10.1731 | 10.1731 | 7 | 0.00021154 | 0.0038077 | 3.8077 | 68.81% | 54.4334 | 0.097874 | 462.6794 | 144.314 | 144.314
55 | 10.0481 | 3.3494 |  | 311.3494 | 10.3494 | 10.3494 | 7 | 0.00021154 | 0.0040192 | 4.0192 | 67.64% | 54.4019 | 0.098413 | 465.2236 | 150.5601 | 150.5601
55 | 10.5769 | 3.5256 |  | 311.5256 | 10.5256 | 10.5256 | 7 | 0.00021154 | 0.0042308 | 4.2308 | 66.5% | 54.3704 | 0.098911 | 467.5814 | 156.6198 | 156.6198
55 | 11.1058 | 3.7019 |  | 311.7019 | 10.7019 | 10.7019 | 7 | 0.00021154 | 0.0044423 | 4.4423 | 65.41% | 54.3389 | 0.099371 | 469.7527 | 162.4931 | 162.4931
55 | 11.6346 | 3.8782 |  | 311.8782 | 10.8782 | 10.8782 | 7 | 0.00021154 | 0.0046538 | 4.6538 | 64.35% | 54.3075 | 0.099791 | 471.7375 | 168.1799 | 168.1799
55 | 12.1635 | 4.0545 |  | 312.0545 | 11.0545 | 11.0545 | 7 | 0.00021154 | 0.0048654 | 4.8654 | 63.32% | 54.276 | 0.10017 | 473.536 | 173.6802 | 173.6802
55 | 12.6923 | 4.2308 |  | 312.2308 | 11.2308 | 11.2308 | 7 | 0.00021154 | 0.0050769 | 5.0769 | 62.33% | 54.2445 | 0.10051 | 475.1479 | 178.9941 | 178.9941
55 | 13.2212 | 4.4071 |  | 312.4071 | 11.4071 | 11.4071 | 7 | 0.00021154 | 0.0052885 | 5.2885 | 61.37% | 54.213 | 0.10081 | 476.5734 | 184.1215 | 184.1215
55 | 13.75 | 4.5833 |  | 312.5833 | 11.5833 | 11.5833 | 7 | 0.00021154 | 0.0055 | 5.5 | 60.43% | 54.1815 | 0.10108 | 477.8125 | 189.0625 | 189.0625
55 | 14.2788 | 4.7596 |  | 312.7596 | 11.7596 | 11.7596 | 7 | 0.00021154 | 0.0057115 | 5.7115 | 59.53% | 54.1501 | 0.1013 | 478.8651 | 193.817 | 193.817
55 | 14.8077 | 4.9359 |  | 312.9359 | 11.9359 | 11.9359 | 7 | 0.00021154 | 0.0059231 | 5.9231 | 58.65% | 54.1186 | 0.10148 | 479.7313 | 198.3851 | 198.3851
55 | 15.3365 | 5.1122 |  | 313.1122 | 12.1122 | 12.1122 | 7 | 0.00021154 | 0.0061346 | 6.1346 | 57.79% | 54.0871 | 0.10163 | 480.411 | 202.7667 | 202.7667
55 | 15.8654 | 5.2885 |  | 313.2885 | 12.2885 | 12.2885 | 7 | 0.00021154 | 0.0063462 | 6.3462 | 56.96% | 54.0556 | 0.10173 | 480.9042 | 206.9619 | 206.9619
55 | 16.3942 | 5.4647 |  | 313.4647 | 12.4647 | 12.4647 | 7 | 0.00021154 | 0.0065577 | 6.5577 | 56.16% | 54.0242 | 0.10179 | 481.211 | 210.9706 | 210.9706
55 | 16.9231 | 5.641 |  | 313.641 | 12.641 | 12.641 | 7 | 0.00021154 | 0.0067692 | 6.7692 | 55.38% | 53.9927 | 0.10182 | 481.3314 | 214.7929 | 214.7929
55 | 17.4519 | 5.8173 |  | 313.8173 | 12.8173 | 12.8173 | 7 | 0.00021154 | 0.0069808 | 6.9808 | 54.61% | 53.9612 | 0.10181 | 481.2653 | 218.4287 | 218.4287
55 | 17.9808 | 5.9936 |  | 313.9936 | 12.9936 | 12.9936 | 7 | 0.00021154 | 0.0071923 | 7.1923 | 53.87% | 53.9297 | 0.10175 | 481.0127 | 221.8781 | 221.8781
55 | 18.5096 | 6.1699 |  | 314.1699 | 13.1699 | 13.1699 | 7 | 0.00021154 | 0.0074038 | 7.4038 | 53.15% | 53.8982 | 0.10166 | 480.5737 | 225.141 | 225.141
55 | 19.0385 | 6.3462 |  | 314.3462 | 13.3462 | 13.3462 | 7 | 0.00021154 | 0.0076154 | 7.6154 | 52.45% | 53.8668 | 0.10153 | 479.9482 | 228.2175 | 228.2175
55 | 19.5673 | 6.5224 |  | 314.5224 | 13.5224 | 13.5224 | 7 | 0.00021154 | 0.0078269 | 7.8269 | 51.77% | 53.8353 | 0.10136 | 479.1363 | 231.1075 | 231.1075
55 | 20.0962 | 6.6987 |  | 314.6987 | 13.6987 | 13.6987 | 7 | 0.00021154 | 0.0080385 | 8.0385 | 51.1% | 53.8038 | 0.10114 | 478.1379 | 233.811 | 233.811
55 | 20.625 | 6.875 |  | 314.875 | 13.875 | 13.875 | 7 | 0.00021154 | 0.00825 | 8.25 | 50.45% | 53.7723 | 0.10089 | 476.9531 | 236.3281 | 236.3281
55 | 21.1538 | 7.0513 |  | 315.0513 | 14.0513 | 14.0513 | 7 | 0.00021154 | 0.0084615 | 8.4615 | 49.82% | 53.7408 | 0.1006 | 475.5819 | 238.6588 | 238.6588
55 | 21.6827 | 7.2276 |  | 315.2276 | 14.2276 | 14.2276 | 7 | 0.00021154 | 0.0086731 | 8.6731 | 49.2% | 53.7094 | 0.10027 | 474.0241 | 240.803 | 240.803
55 | 22.2115 | 7.4038 |  | 315.4038 | 14.4038 | 14.4038 | 7 | 0.00021154 | 0.0088846 | 8.8846 | 48.6% | 53.6779 | 0.099905 | 472.28 | 242.7607 | 242.7607
55 | 22.7404 | 7.5801 |  | 315.5801 | 14.5801 | 14.5801 | 7 | 0.00021154 | 0.0090962 | 9.0962 | 48.01% | 53.6464 | 0.099497 | 470.3493 | 244.532 | 244.532
55 | 23.2692 | 7.7564 |  | 315.7564 | 14.7564 | 14.7564 | 7 | 0.00021154 | 0.0093077 | 9.3077 | 47.44% | 53.6149 | 0.099049 | 468.2322 | 246.1169 | 246.1169
55 | 23.7981 | 7.9327 |  | 315.9327 | 14.9327 | 14.9327 | 7 | 0.00021154 | 0.0095192 | 9.5192 | 46.88% | 53.5834 | 0.098562 | 465.9287 | 247.5153 | 247.5153
55 | 24.3269 | 8.109 |  | 316.109 | 15.109 | 15.109 | 7 | 0.00021154 | 0.0097308 | 9.7308 | 46.33% | 53.552 | 0.098035 | 463.4387 | 248.7272 | 248.7272
55 | 24.8558 | 8.2853 |  | 316.2853 | 15.2853 | 15.2853 | 7 | 0.00021154 | 0.0099423 | 9.9423 | 45.8% | 53.5205 | 0.097469 | 460.7623 | 249.7527 | 249.7527
55 | 25.3846 | 8.4615 |  | 316.4615 | 15.4615 | 15.4615 | 7 | 0.00021154 | 0.010154 | 10.1538 | 45.27% | 53.489 | 0.096863 | 457.8994 | 250.5917 | 250.5917
55 | 25.9135 | 8.6378 |  | 316.6378 | 15.6378 | 15.6378 | 7 | 0.00021154 | 0.010365 | 10.3654 | 44.76% | 53.4575 | 0.096218 | 454.8501 | 251.2443 | 251.2443
55 | 26.4423 | 8.8141 |  | 316.8141 | 15.8141 | 15.8141 | 7 | 0.00021154 | 0.010577 | 10.5769 | 44.26% | 53.4261 | 0.095534 | 451.6143 | 251.7104 | 251.7104
55 | 26.9712 | 8.9904 |  | 316.9904 | 15.9904 | 15.9904 | 7 | 0.00021154 | 0.010788 | 10.7885 | 43.78% | 53.3946 | 0.09481 | 448.192 | 251.9901 | 251.9901
55 | 27.5 | 9.1667 |  | 317.1667 | 16.1667 | 16.1667 | 7 | 0.00021154 | 0.011 | 11 | 43.3% | 53.3631 | 0.094046 | 444.5833 | 252.0833 | 252.0833
55 | 28.0288 | 9.3429 |  | 317.3429 | 16.3429 | 16.3429 | 7 | 0.00021154 | 0.011212 | 11.2115 | 42.83% | 53.3316 | 0.093244 | 440.7882 | 251.9901 | 251.9901
55 | 28.5577 | 9.5192 |  | 317.5192 | 16.5192 | 16.5192 | 7 | 0.00021154 | 0.011423 | 11.4231 | 42.37% | 53.3001 | 0.092401 | 436.8066 | 251.7104 | 251.7104
55 | 29.0865 | 9.6955 |  | 317.6955 | 16.6955 | 16.6955 | 7 | 0.00021154 | 0.011635 | 11.6346 | 41.93% | 53.2687 | 0.09152 | 432.6385 | 251.2443 | 251.2443
55 | 29.6154 | 9.8718 |  | 317.8718 | 16.8718 | 16.8718 | 7 | 0.00021154 | 0.011846 | 11.8462 | 41.49% | 53.2372 | 0.090599 | 428.284 | 250.5917 | 250.5917
55 | 30.1442 | 10.0481 |  | 318.0481 | 17.0481 | 17.0481 | 7 | 0.00021154 | 0.012058 | 12.0577 | 41.06% | 53.2057 | 0.089638 | 423.7431 | 249.7527 | 249.7527
55 | 30.6731 | 10.2244 |  | 318.2244 | 17.2244 | 17.2244 | 7 | 0.00021154 | 0.012269 | 12.2692 | 40.64% | 53.1742 | 0.088638 | 419.0157 | 248.7272 | 248.7272
55 | 31.2019 | 10.4006 |  | 318.4006 | 17.4006 | 17.4006 | 7 | 0.00021154 | 0.012481 | 12.4808 | 40.23% | 53.1427 | 0.087598 | 414.1018 | 247.5153 | 247.5153
55 | 31.7308 | 10.5769 |  | 318.5769 | 17.5769 | 17.5769 | 7 | 0.00021154 | 0.012692 | 12.6923 | 39.82% | 53.1113 | 0.08652 | 409.0015 | 246.1169 | 246.1169
55 | 32.2596 | 10.7532 |  | 318.7532 | 17.7532 | 17.7532 | 7 | 0.00021154 | 0.012904 | 12.9038 | 39.43% | 53.0798 | 0.085401 | 403.7147 | 244.532 | 244.532
55 | 32.7885 | 10.9295 |  | 318.9295 | 17.9295 | 17.9295 | 7 | 0.00021154 | 0.013115 | 13.1154 | 39.04% | 53.0483 | 0.084243 | 398.2415 | 242.7607 | 242.7607
55 | 33.3173 | 11.1058 |  | 319.1058 | 18.1058 | 18.1058 | 7 | 0.00021154 | 0.013327 | 13.3269 | 38.66% | 53.0168 | 0.083046 | 392.5818 | 240.803 | 240.803
55 | 33.8462 | 11.2821 |  | 319.2821 | 18.2821 | 18.2821 | 7 | 0.00021154 | 0.013538 | 13.5385 | 38.29% | 52.9853 | 0.081809 | 386.7357 | 238.6588 | 238.6588
55 | 34.375 | 11.4583 |  | 319.4583 | 18.4583 | 18.4583 | 7 | 0.00021154 | 0.01375 | 13.75 | 37.92% | 52.9539 | 0.080533 | 380.7031 | 236.3281 | 236.3281
55 | 34.9038 | 11.6346 |  | 319.6346 | 18.6346 | 18.6346 | 7 | 0.00021154 | 0.013962 | 13.9615 | 37.56% | 52.9224 | 0.079218 | 374.4841 | 233.811 | 233.811
55 | 35.4327 | 11.8109 |  | 319.8109 | 18.8109 | 18.8109 | 7 | 0.00021154 | 0.014173 | 14.1731 | 37.21% | 52.8909 | 0.077863 | 368.0786 | 231.1075 | 231.1075
55 | 35.9615 | 11.9872 |  | 319.9872 | 18.9872 | 18.9872 | 7 | 0.00021154 | 0.014385 | 14.3846 | 36.87% | 52.8594 | 0.076468 | 361.4867 | 228.2175 | 228.2175
55 | 36.4904 | 12.1635 |  | 320.1635 | 19.1635 | 19.1635 | 7 | 0.00021154 | 0.014596 | 14.5962 | 36.53% | 52.828 | 0.075034 | 354.7083 | 225.141 | 225.141
55 | 37.0192 | 12.3397 |  | 320.3397 | 19.3397 | 19.3397 | 7 | 0.00021154 | 0.014808 | 14.8077 | 36.19% | 52.7965 | 0.073561 | 347.7435 | 221.8781 | 221.8781
55 | 37.5481 | 12.516 |  | 320.516 | 19.516 | 19.516 | 7 | 0.00021154 | 0.015019 | 15.0192 | 35.87% | 52.765 | 0.072048 | 340.5922 | 218.4287 | 218.4287
55 | 38.0769 | 12.6923 |  | 320.6923 | 19.6923 | 19.6923 | 7 | 0.00021154 | 0.015231 | 15.2308 | 35.55% | 52.7335 | 0.070496 | 333.2544 | 214.7929 | 214.7929
55 | 38.6058 | 12.8686 |  | 320.8686 | 19.8686 | 19.8686 | 7 | 0.00021154 | 0.015442 | 15.4423 | 35.23% | 52.702 | 0.068904 | 325.7302 | 210.9706 | 210.9706
55 | 39.1346 | 13.0449 |  | 321.0449 | 20.0449 | 20.0449 | 7 | 0.00021154 | 0.015654 | 15.6538 | 34.92% | 52.6706 | 0.067273 | 318.0196 | 206.9619 | 206.9619
55 | 39.6635 | 13.2212 |  | 321.2212 | 20.2212 | 20.2212 | 7 | 0.00021154 | 0.015865 | 15.8654 | 34.62% | 52.6391 | 0.065603 | 310.1225 | 202.7667 | 202.7667
55 | 40.1923 | 13.3974 |  | 321.3974 | 20.3974 | 20.3974 | 7 | 0.00021154 | 0.016077 | 16.0769 | 34.32% | 52.6076 | 0.063893 | 302.039 | 198.3851 | 198.3851
55 | 40.7212 | 13.5737 |  | 321.5737 | 20.5737 | 20.5737 | 7 | 0.00021154 | 0.016288 | 16.2885 | 34.02% | 52.5761 | 0.062143 | 293.769 | 193.817 | 193.817
55 | 41.25 | 13.75 |  | 321.75 | 20.75 | 20.75 | 7 | 0.00021154 | 0.0165 | 16.5 | 33.73% | 52.5446 | 0.060355 | 285.3125 | 189.0625 | 189.0625
55 | 41.7788 | 13.9263 |  | 321.9263 | 20.9263 | 20.9263 | 7 | 0.00021154 | 0.016712 | 16.7115 | 33.45% | 52.5132 | 0.058526 | 276.6696 | 184.1215 | 184.1215
55 | 42.3077 | 14.1026 |  | 322.1026 | 21.1026 | 21.1026 | 7 | 0.00021154 | 0.016923 | 16.9231 | 33.17% | 52.4817 | 0.056659 | 267.8402 | 178.9941 | 178.9941
55 | 42.8365 | 14.2788 |  | 322.2788 | 21.2788 | 21.2788 | 7 | 0.00021154 | 0.017135 | 17.1346 | 32.9% | 52.4502 | 0.054751 | 258.8244 | 173.6802 | 173.6802
55 | 43.3654 | 14.4551 |  | 322.4551 | 21.4551 | 21.4551 | 7 | 0.00021154 | 0.017346 | 17.3462 | 32.63% | 52.4187 | 0.052805 | 249.6222 | 168.1799 | 168.1799
55 | 43.8942 | 14.6314 |  | 322.6314 | 21.6314 | 21.6314 | 7 | 0.00021154 | 0.017558 | 17.5577 | 32.36% | 52.3872 | 0.050819 | 240.2335 | 162.4931 | 162.4931
55 | 44.4231 | 14.8077 |  | 322.8077 | 21.8077 | 21.8077 | 7 | 0.00021154 | 0.017769 | 17.7692 | 32.1% | 52.3558 | 0.048793 | 230.6583 | 156.6198 | 156.6198
55 | 44.9519 | 14.984 |  | 322.984 | 21.984 | 21.984 | 7 | 0.00021154 | 0.017981 | 17.9808 | 31.84% | 52.3243 | 0.046728 | 220.8967 | 150.5601 | 150.5601
55 | 45.4808 | 15.1603 |  | 323.1603 | 22.1603 | 22.1603 | 7 | 0.00021154 | 0.018192 | 18.1923 | 31.59% | 52.2928 | 0.044624 | 210.9486 | 144.314 | 144.314
55 | 46.0096 | 15.3365 |  | 323.3365 | 22.3365 | 22.3365 | 7 | 0.00021154 | 0.018404 | 18.4038 | 31.34% | 52.2613 | 0.04248 | 200.8141 | 137.8814 | 137.8814
55 | 46.5385 | 15.5128 |  | 323.5128 | 22.5128 | 22.5128 | 7 | 0.00021154 | 0.018615 | 18.6154 | 31.09% | 52.2299 | 0.040297 | 190.4931 | 131.2623 | 131.2623
55 | 47.0673 | 15.6891 |  | 323.6891 | 22.6891 | 22.6891 | 7 | 0.00021154 | 0.018827 | 18.8269 | 30.85% | 52.1984 | 0.038074 | 179.9857 | 124.4568 | 124.4568
55 | 47.5962 | 15.8654 |  | 323.8654 | 22.8654 | 22.8654 | 7 | 0.00021154 | 0.019038 | 19.0385 | 30.61% | 52.1669 | 0.035812 | 169.2918 | 117.4649 | 117.4649
55 | 48.125 | 16.0417 |  | 324.0417 | 23.0417 | 23.0417 | 7 | 0.00021154 | 0.01925 | 19.25 | 30.38% | 52.1354 | 0.03351 | 158.4115 | 110.2865 | 110.2865
55 | 48.6538 | 16.2179 |  | 324.2179 | 23.2179 | 23.2179 | 7 | 0.00021154 | 0.019462 | 19.4615 | 30.15% | 52.1039 | 0.031169 | 147.3447 | 102.9216 | 102.9216
55 | 49.1827 | 16.3942 |  | 324.3942 | 23.3942 | 23.3942 | 7 | 0.00021154 | 0.019673 | 19.6731 | 29.92% | 52.0725 | 0.028789 | 136.0914 | 95.3703 | 95.3703
55 | 49.7115 | 16.5705 |  | 324.5705 | 23.5705 | 23.5705 | 7 | 0.00021154 | 0.019885 | 19.8846 | 29.7% | 52.041 | 0.026369 | 124.6518 | 87.6325 | 87.6325
55 | 50.2404 | 16.7468 |  | 324.7468 | 23.7468 | 23.7468 | 7 | 0.00021154 | 0.020096 | 20.0962 | 29.48% | 52.0095 | 0.023909 | 113.0256 | 79.7083 | 79.7083
55 | 50.7692 | 16.9231 |  | 324.9231 | 23.9231 | 23.9231 | 7 | 0.00021154 | 0.020308 | 20.3077 | 29.26% | 51.978 | 0.02141 | 101.213 | 71.5976 | 71.5976
55 | 51.2981 | 17.0994 |  | 325.0994 | 24.0994 | 24.0994 | 7 | 0.00021154 | 0.020519 | 20.5192 | 29.05% | 51.9465 | 0.018872 | 89.214 | 63.3005 | 63.3005
55 | 51.8269 | 17.2756 |  | 325.2756 | 24.2756 | 24.2756 | 7 | 0.00021154 | 0.020731 | 20.7308 | 28.84% | 51.9151 | 0.016294 | 77.0285 | 54.8169 | 54.8169
55 | 52.3558 | 17.4519 |  | 325.4519 | 24.4519 | 24.4519 | 7 | 0.00021154 | 0.020942 | 20.9423 | 28.63% | 51.8836 | 0.013677 | 64.6565 | 46.1469 | 46.1469
55 | 52.8846 | 17.6282 |  | 325.6282 | 24.6282 | 24.6282 | 7 | 0.00021154 | 0.021154 | 21.1538 | 28.42% | 51.8521 | 0.011021 | 52.0981 | 37.2904 | 37.2904
55 | 53.4135 | 17.8045 |  | 325.8045 | 24.8045 | 24.8045 | 7 | 0.00021154 | 0.021365 | 21.3654 | 28.22% | 51.8206 | 0.0083247 | 39.3533 | 28.2475 | 28.2475
55 | 53.9423 | 17.9808 |  | 325.9808 | 24.9808 | 24.9808 | 7 | 0.00021154 | 0.021577 | 21.5769 | 28.02% | 51.7891 | 0.0055893 | 26.422 | 19.0181 | 19.0181
55 | 54.4712 | 18.1571 |  | 326.1571 | 25.1571 | 25.1571 | 7 | 0.00021154 | 0.021788 | 21.7885 | 27.83% | 51.7577 | 0.0028144 | 13.3042 | 9.6023 | 9.6023
55 | 55 | 18.3333 |  | 326.3333 | 25.3333 | 25.3333 | 7 | 0.00021154 | 0.022 | 22 | 27.63% | 51.7262 | 0 | 0 | 0 | 0
[10 empty] | 22.5 |  |  | 0 | 0

## SOA (hidden)
|  | Look Up |  |  |  |  | I = a * t^m
| 100us | 1ms | 10ms | 100ms | 1s/DC |  | a = iSOA1/tSOA1^m
Final SOA | 100 | 8 | 2 | 2 | 2 |  | m = log(iSOA1/iSOA2)/log(tSOA1/tSOA2)
| SOA Check - Based on Timer |  |  |  |  | SOA Predictor - dv/dt start-up
| time | #REF! | ms |  |  | time | 16.1339 | ms
| Voltage | 55 | V |  |  | Voltage | 55 | V
| Lower time | #REF! | ms |  |  | Lower time | 10 | ms
| Lower time (adjusted) | #REF! |  |  |  | Lower time (adjusted) | 10
| Higher timer | #REF! | ms |  |  | Higher time | 100 | ms
| Higher time (adjusted) | #REF! |  |  |  | Higher time (adjusted) | 100
| I (lower time) | #REF! | A |  |  | I (lower time) | 2 | A
| I (higher time) | #REF! | A |  |  | I (higher time) | 2 | A
| Assuming Power vs time is linear on a log-log plot |  |  |  |  | Assuming Power vs time is linear on a log-log plot
| a | #REF! |  |  |  | a | 2
| m | #REF! |  |  |  | m | 1e-12 | <-- Cannot plot zero on a log graph. If slope ~=0, then use 1e-12 as value
| Extr. I | #REF! | A |  |  | Extr. I | 2
| Interpolated Power= | #REF! |  |  |  | Interpolated Power= | 110
[6 empty] | board hot? | 0.5
| Derating factor = | 0.48333 |  |  |  | Temp for derating | 55
| Max Power with Temp Derating = | #REF! | W
[6 empty] | Derating factor = | 0.8
[6 empty] | Max Power with Temp Derating = | 88
SOA Coefficients
|  | 0.1 to 1 ms | 1 to 10ms | 10ms to 100 ms | 100 ms to 1s
| t1 | 0.1 | 1 | 10 | 100
| t2 | 1 | 10 | 100 | 1000
| a | 8 | 8 | 2 | 2
| m | -1.0969 | -0.60206 | 0 | 0
| MOSFET's SOA |  |  |  |  | MOSFET's SOA
| VDS | ID |  |  |  | VDS | ID
| (V) | (A) |  |  |  | (V) | (A)
| 1 | #REF! |  |  |  | 1 | 88
| 1.2 | #REF! |  |  |  | 1.2 | 73.3333
| 30 | #REF! |  |  |  | 30 | 2.9333
Note on C39: Enter data from the MOSFET's SOA chart typically found in its datasheet. Consult the MOSFET vendor for SOA performance detail and appropriate derating criteria.
Note on H39: Enter data from the MOSFET's SOA chart typically found in its datasheet. Consult the MOSFET vendor for SOA performance detail and appropriate derating criteria.
Note on C40: Enter data from the MOSFET's SOA chart typically found in its datasheet. Consult the MOSFET vendor for SOA performance detail and appropriate derating criteria.
Note on H40: Enter data from the MOSFET's SOA chart typically found in its datasheet. Consult the MOSFET vendor for SOA performance detail and appropriate derating criteria.
Note on C41: Enter data from the MOSFET's SOA chart typically found in its datasheet. Consult the MOSFET vendor for SOA performance detail and appropriate derating criteria.
Note on H41: Enter data from the MOSFET's SOA chart typically found in its datasheet. Consult the MOSFET vendor for SOA performance detail and appropriate derating criteria.

## dv_dt_recommendations (hidden)
Key Equations for SOA margin estimate:
1) Get total Energy = 1/2 CV^2 + E_load (t_worksheet) * t_start / t_ worksheet
note: t_worksheet is the start time from the start-up worksheet. E_load = Total Energy @ Start-up - 1/2CV^2
2) Get peak power: 4 Possible points with peak power
a) At Vin = 0 [mainly if there is no load or constant current load that starts at Vout = 0=
b) At Vin = Load start [ constant current=
c) When derivative of power = 0 [Peak, applies to resistive loads only=
P = (I_cap + Vout/R ) * (Vin - Vout) = Icap * Vin - Icap * Vout +Vin * Vout / R - Vout^2 / R
=> dP/dVout = -Icap + Vin/R -2Vout /R ; Zero when Vout = -R*I_cap / 2 + Vin / 2
Copied Inputs
| Temp_start_up | 55
| SOA margin target | 1.3 |  |  |  | SOA Coefficients
| Cap Energy (J) | 4.235 |  |  |  |  | 0.1 to 1 ms | 1 to 10ms | 10ms to 100 ms | 100 ms to 1s
| E_load (t_worksheet) (J) | 3.5308 |  |  |  | t1 | 0.1 | 1 | 10 | 100
| t_worksheet (ms) | 22 |  |  |  | t2 | 1 | 10 | 100 | 1000
[6 empty] | a | 8 | 8 | 2 | 2
| Load Turn-On Threshold | 6 |  |  |  | m | -1.0969 | -0.60206 | 0 | 0
| Startup Load Type | Resistive
| Startup Load Value | 3 |  |  |  | Initial | Final
|  |  |  | max slew rate |  | 0 | NA
| Upper bound Slew Rate (4ms start-up) (V/ms) | 12 |  | min slew rate |  | 0 | NA
| Min Slew Rate (400 ms start - up) (V/ms) | 0.06
| # of points | 20
| mult per point | 0.75665
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| slew rate (V/ms) | 12 | 9.0798 | 6.8702 | 5.1983 | 3.9333 | 2.9761 | 2.2519 | 1.7039 | 1.2892 | 0.97548 | 0.7381 | 0.55848 | 0.42257 | 0.31974 | 0.24193 | 0.18305 | 0.13851 | 0.1048 | 0.079297 | 0.06
| t_start (ms) | 4.5833 | 6.0574 | 8.0056 | 10.5804 | 13.9833 | 18.4806 | 24.4243 | 32.2797 | 42.6615 | 56.3823 | 74.5161 | 98.482 | 130.1558 | 172.0166 | 227.3407 | 300.4582 | 397.0918 | 524.8047 | 693.5928 | 916.6667
| I_cap (A) | 33.6 | 25.4233 | 19.2365 | 14.5552 | 11.0132 | 8.3331 | 6.3052 | 4.7708 | 3.6098 | 2.7314 | 2.0667 | 1.5637 | 1.1832 | 0.89526 | 0.6774 | 0.51255 | 0.38782 | 0.29344 | 0.22203 | 0.168
| Total FET Energy (J) | 4.9706 | 5.2072 | 5.5198 | 5.933 | 6.4792 | 7.2009 | 8.1549 | 9.4156 | 11.0817 | 13.2838 | 16.1941 | 20.0403 | 25.1237 | 31.8419 | 40.7208 | 52.4555 | 67.9641 | 88.4608 | 115.5495 | 151.3506
| Power (Vout= 0) , (W) | 1848 | 1398.2832 | 1058.0064 | 800.5371 | 605.7237 | 458.3189 | 346.7855 | 262.3941 | 198.5396 | 150.2244 | 113.6668 | 86.0056 | 65.0759 | 49.2394 | 37.2569 | 28.1903 | 21.3301 | 16.1393 | 12.2118 | 9.24
| Power (load on), (W) | 1744.4 | 1343.7432 | 1040.5875 | 811.2057 | 637.6448 | 506.3205 | 406.9543 | 331.7693 | 274.8808 | 231.8363 | 199.2668 | 174.6232 | 155.9767 | 141.8679 | 131.1925 | 123.115 | 117.0032 | 112.3787 | 108.8796 | 106.232
| Vout (dP/dVout = 0) (V) | -22.9 | -10.635 | -1.3547 | 5.6672 | 10.9803 | 15.0004 | 18.0422 | 20.3438 | 22.0853 | 23.403 | 24.4 | 25.1544 | 25.7252 | 26.1571 | 26.4839 | 26.7312 | 26.9183 | 27.0598 | 27.167 | 27.248
| Power (@ Vout above, if applicable) | 0 | 0 | 0 | 0 | 645.9125 | 533.3228 | 455.2926 | 400.3508 | 361.1262 | 332.7907 | 312.1201 | 296.9201 | 285.6712 | 277.3042 | 271.0559 | 266.3755 | 262.8612 | 260.2176 | 258.2262 | 256.7245
| max power (W) | 1848 | 1398.2832 | 1058.0064 | 811.2057 | 645.9125 | 533.3228 | 455.2926 | 400.3508 | 361.1262 | 332.7907 | 312.1201 | 296.9201 | 285.6712 | 277.3042 | 271.0559 | 266.3755 | 262.8612 | 260.2176 | 258.2262 | 256.7245
| Equivalent time for SOA (ms) | 2.6897 | 3.724 | 5.2172 | 7.3139 | 10.031 | 13.502 | 17.9112 | 23.5183 | 30.6866 | 39.9163 | 51.8841 | 67.4941 | 87.9461 | 114.8266 | 150.2304 | 196.923 | 258.5553 | 339.9492 | 447.474 | 589.5447
| a | 8 | 8 | 8 | 8 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| m | -0.60206 | -0.60206 | -0.60206 | -0.60206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Available SOA (W) | 242.5183 | 199.3761 | 162.7469 | 132.7959 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
| Derated for Temp | 194.0147 | 159.5009 | 130.1975 | 106.2367 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
| SOA Margin | 0.10499 | 0.11407 | 0.12306 | 0.13096 | 0.13624 | 0.165 | 0.19328 | 0.21981 | 0.24368 | 0.26443 | 0.28194 | 0.29638 | 0.30805 | 0.31734 | 0.32466 | 0.33036 | 0.33478 | 0.33818 | 0.34079 | 0.34278
| Pass? | [20 empty] | N | bar: 0.75665 1 to 0.75665 20
| first yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2nd yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mult 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| mult2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Cap Tables (hidden)
Standard Capacitor Values
pF | nF | µF | mF
1 | 1 | 1 | 1
1.1 | 1.1 | 1
1.2 | 1.2 | 1
1.3 | 1.3 | 1
1.5 | 1.5 | 1.5 | 1.5
1.6 | 1.6 | 1.5
1.8 | 1.8 | 1.5
2 | 2 | 1.5
2.2 | 2.2 | 2.2 | 2.2
2.4 | 2.4 | 2.2
2.7 | 2.7 | 2.2
3 | 3 | 2.2
3.3 | 3.3 | 3.3 | 3.3
3.6 | 3.6 | 4.7
3.9 | 3.9 | 4.7
4.3 | 4.3 | 4.7
4.7 | 4.7 | 4.7 | 4.7
5.1 | 5.1 | 6.8
5.6 | 5.6 | 6.8
6.2 | 6.2 | 6.8
6.8 | 6.8 | 6.8 | 6.8
7.5 | 7.5 | 10
8.2 | 8.2 | 10
9.1 | 9.1 | 10
10 | 10 | 10 | 10
11 | 15 | 15
12 | 15 | 15
13 | 15 | 15
15 | 15 | 15
16 | 22 | 22
18 | 22 | 22
20 | 22 | 22
22 | 22 | 22
24 | 33 | 33
27 | 33 | 33
30 | 33 | 33
33 | 33 | 33
36 | 47 | 47
39 | 47 | 47
43 | 47 | 47
47 | 47 | 47
51 | 68 | 68
56 | 68 | 68
62 | 68 | 68
68 | 68 | 68
75 | 100 | 100
82 | 100 | 100
91 | 100 | 100
100 | 100 | 100
110 | 150 | 150
120 | 150 | 150
130 | 150 | 150
150 | 150 | 150
160 | 220 | 220
180 | 220 | 220
200 | 220 | 220
220 | 220 | 220
240 | 330 | 330
270 | 330 | 330
300 | 330 | 330
330 | 330 | 330
360 | 470 | 470
390 | 470 | 470
430 | 470 | 470
470 | 470 | 470
510 | 680 | 680
560 | 680 | 680
620 | 680 | 680
680 | 680 | 680
750 | 1000 | 1000
820 | 1000 | 1000
910 | 1000 | 1000

## Res EIA Tables (hidden)
Standard EIA Decade Resistor Values
20% | 10% | 5% | 2% | 1% | 0.5%, 0.25%, 0.1%
E6 | E12 | E24 | E48 | E96 | E192
100 | 100 | 100 | 100 | 100 | 100
101
|  |  |  | 102 | 102
104
|  |  | 105 | 105 | 105
106
|  |  |  | 107 | 107
109
|  | 110 | 110 | 110 | 110
111
|  |  |  | 113 | 113
114
|  |  | 115 | 115 | 115
117
|  |  |  | 118 | 118
120
| 120 | 120 | 121 | 121 | 121
123
|  |  |  | 124 | 124
126
|  |  | 127 | 127 | 127
129
|  |  |  | 130 | 130
132
|  | 130 | 133 | 133 | 133
135
|  |  |  | 137 | 137
138
|  |  | 140 | 140 | 140
142
|  |  |  | 143 | 143
145
150 | 150 | 150 | 147 | 147 | 147
149
|  |  |  | 150 | 150
152
|  |  | 154 | 154 | 154
156
|  |  |  | 158 | 158
160
|  | 160 | 162 | 162 | 162
164
|  |  |  | 165 | 165
167
|  |  | 169 | 169 | 169
172
|  |  |  | 174 | 174
176
| 180 | 180 | 178 | 178 | 178
180
|  |  |  | 182 | 182
184
|  |  | 187 | 187 | 187
189
|  |  |  | 191 | 191
193
|  | 200 | 196 | 196 | 196
198
|  |  |  | 200 | 200
203
|  |  | 205 | 205 | 205
208
|  |  |  | 210 | 210
213
220 | 220 | 220 | 215 | 215 | 215
218
|  |  |  | 221 | 221
223
|  |  | 226 | 226 | 226
229
|  |  |  | 232 | 232
234
|  | 240 | 237 | 237 | 237
240
|  |  |  | 243 | 243
246
|  |  | 249 | 249 | 249
252
|  |  |  | 255 | 255
258
| 270 | 270 | 261 | 261 | 261
264
|  |  |  | 267 | 267
271
|  |  | 274 | 274 | 274
277
|  |  |  | 280 | 280
284
|  | 300 | 287 | 287 | 287
291
|  |  |  | 294 | 294
298
|  |  | 301 | 301 | 301
305
|  |  |  | 309 | 309
312
330 | 330 | 330 | 316 | 316 | 316
320
|  |  |  | 324 | 324
328
|  |  | 332 | 332 | 332
336
|  |  |  | 340 | 340
344
|  | 360 | 348 | 348 | 348
352
|  |  |  | 357 | 357
361
|  |  | 365 | 365 | 365
370
|  |  |  | 374 | 374
379
| 390 | 390 | 383 | 383 | 383
388
|  |  |  | 392 | 392
397
|  |  | 402 | 402 | 402
407
|  |  |  | 412 | 412
417
|  | 430 | 422 | 422 | 422
427
|  |  |  | 432 | 432
437
|  |  | 442 | 442 | 442
448
|  |  |  | 453 | 453
459
470 | 470 | 470 | 464 | 464 | 464
470
|  |  |  | 475 | 475
481
|  |  | 487 | 487 | 487
493
|  |  |  | 499 | 499
505
|  | 510 | 511 | 511 | 511
517
|  |  |  | 523 | 523
530
|  |  | 536 | 536 | 536
542
|  |  |  | 549 | 549
556
| 560 | 560 | 562 | 562 | 562
569
|  |  |  | 576 | 576
583
|  |  | 590 | 590 | 590
597
|  |  |  | 604 | 604
612
|  | 620 | 619 | 619 | 619
626
|  |  |  | 634 | 634
642
|  |  | 649 | 649 | 649
657
|  |  |  | 665 | 665
673
680 | 680 | 680 | 681 | 681 | 681
690
|  |  |  | 698 | 698
706
|  |  | 715 | 715 | 715
723
|  |  |  | 732 | 732
741
|  | 750 | 750 | 750 | 750
759
|  |  |  | 768 | 768
777
|  |  | 787 | 787 | 787
796
|  |  |  | 806 | 806
816
| 820 | 820 | 825 | 825 | 825
835
|  |  |  | 845 | 845
856
|  |  | 866 | 866 | 866
876
|  |  |  | 887 | 887
898
|  | 910 | 909 | 909 | 909
920
|  |  |  | 931 | 931
942
|  |  | 953 | 953 | 953
965
|  |  |  | 976 | 976
988
1000 | 1000 | 1000 | 1000 | 1000 | 1000 | End Values Required for Processing