## Component_Selection
TPS2352x Hot Swap Design Tool
www.ti.com/hotswap
Enter Values in Green Shaded Cells
Calculated Values are shown in White Cells
Yellow and Red cells highlight potential issues with the design. Red highlights items that are higher risk.
|  | System Inputs: | Min | Typ | Max | Units
|  | Load Power |  | 1344 | 1344 | W
|  | Bus Voltage | 38 | 48 | 60 | V
|  | Output Capacitance |  | 660 | 792 | uF
|  | Tamb (Or Tpcb) |  |  | 60 | C
Current Limit & FET:
|  | VSNS,CL1 setting (40mV, only availlabe for TPS23523/21) |  | 40 |  | mV
|  | Calculated Load Current |  | 28 | 35.3684 | A
|  | Target Current Limit |  | 28 |  | A
|  | Calculated Rsns |  | 1.4286 |  | mΩ
|  | Selected Rsns |  | 1 |  | mΩ
|  | Ilim (high Vds) |  | 40 |  | A
|  | Ilim (low Vds) |  | 3 |  | A
|  | Iin,tmr (where timer trips) | 1.5 |  |  | A
|  | FET (Q1) | CSD19536KTT
|  | Q1 Ron @ Tj,op,max |  |  | 2.25 | mΩ
|  | Q1 Tj,absmax |  |  | 175 | C
|  | Q1 Cgs (Gate to source capacitance) |  |  | 2.4 | nF
|  | # FETs Q1 (driven by GATE) |  | 1 |  |  |  |  | Start - Up
|  | Q2 (only TPS23521/23) | CSD19532Q5B
|  | Q2 Ron @ Tj,op,max (only TPS23521/23) |  |  | 4.6 | mΩ |  | Inrush Current During Start -up (@ max Vin and Cout) |  |  | Q1 Power Dissipation During Start-up
|  | # FETs Q2 (driven by GATE2, only TPS23521/23) |  | 1
|  | Rtheta,ja (OR Psi,j,pcb) |  |  | 50 | C/W
|  | IQ1,max (max current through Q1 "FETs") |  |  | 23.7511 | A
|  | Power Dissipation / FET (Q1) |  |  | 1.2693 | W
Yes |  | Total FET Power Dissipation |  |  | 1.8901 | W
No |  | Tj,op,max (Q1) |  |  | 123.4627 | C
Recommended Timer and Ilim switch
|  | Required to pass ATIS 06003.2013 "Fig 1" or other brown out test? |  |  | No
Targets Below are suggestions only
|  | Suggested Time Out (low Vds) |  |  | 5 | ms
|  | Suggested Ilim switch |  |  | 15 | V
|  | Target Settings: |  | Target
|  | Target UV, rising |  | 41.12 |  | V
|  | Target UV, falling |  | 40.12 |  | V
|  | Target OV, rising |  | 60.45 |  | V
Target |  | Target OV, falling |  | 59.05 |  | V
Programmed |  | Target Ilim, switch |  | 20 |  | V
|  | Target Inrush Current (at max Cout) |  | 0.4 |  | A
|  | Target Time out (low Vds) |  | 2 |  | ms
SOA Margin Check (Refer to SOA margin TAB for full details)
|  | Select, which numbers to use For SOA Margin check & Graphs; "Programmed" = Will use selected Components in Cell E84 to E93. "Target" = Will use target settings from cells E46 to E52. It's recommended to first iterate using target settings. | Programmed
|  | Estimated Teq for Start-into Short |  | 1.0835 |  | ms
|  | Estimated Teq for Start-into 1 ohm short |  | 3.5585 |  | ms
|  | Measured Teq for Start-into Short (Enter TBD if not known) |  | TBD |  | ms
|  | Measured Teq for Start-into 1 ohm short (Enter TBD if not known) |  | TBD |  | ms
|  | Q1 Current handling at 1ms and 60V |  | 10 |  | A
|  | Q1 Current handling at 10ms and 60V |  | 3 |  | A
|  | Q1 Current handling at 1ms and 60V |  | 10 |  | A
|  | Q1 Current handling at 10ms and 60V |  | 3 |  | A
|  | Q1 Current handling at 10ms and 60V |  | 3 |  | A
|  | Q1 Current handling at 100ms and 60V |  | 1 |  | A
|  | Q1 Current handling at 1ms and 20.2V |  | 10 |  | A
|  | Q1 Current handling at 10ms and 20.2V |  | 50 |  | A
|  | SOA Margin: Hot Short / Start-into Short (@ Vin= 60V) |  | 1.0982 |  |  |  |  | Start Into Short with Vin = 60V
|  | SOA Margin: Start-into 1 ohm Short (@ Vin= 60V) |  | 0.58974
|  | SOA Margin: Start-up (@ Vin= 60V) |  | 1.0012
|  | SOA Margin: Current limit (@ Vds just under 20.2V) |  | 0.093266
|  | Start-Time at Max Vin |  | 99 |  | ms
|  | Computed Components: |  | Target
|  | Ruv1 |  | 100 |  | kΩ
|  | Ruv2 |  | 2.4925 |  | kΩ
|  | Rov1 |  | 140 |  | kΩ
|  | Rov2 |  | 2.3549 |  | kΩ
|  | Rd |  | 370 |  | kΩ
|  | Css |  | 39.6 |  | nF
|  | Css,vee |  | 118.8 |  | nF
|  | Ctmr |  | 13.3333 |  | nF
|  | Recommended Rcc (with 20% margin) |  | 22.8182 |  | kΩ
|  | Selected Components: |  | Value | Tol(%)
|  | Rsns |  | 2 | 1% | mΩ
|  | Ruv1 |  | 100 | 0.1% | kΩ
|  | Ruv2 |  | 2.49 | 0.1% | kΩ
|  | Rov1 |  | 140 | 0.1% | kΩ
|  | Rov2 |  | 2.37 | 0.1% | kΩ
|  | Rd |  | 374 | 1% | kΩ |  | Start - Up Using Equivalent Power Pulse (@ Vin,max & Cout,max) |  | SOA with Vds just under 20.2V
|  | Css |  | 33 | 30% | nF
|  | Css,vee |  | 100 | 10% | nF
|  | Ctmr |  | 15 | 10% | nF
|  | Rcc |  | 22.6 | 1% | kΩ
|  | Programmed Settings | Min | Typ | Max |  | Error
|  | Error calculation | RMS
|  | Ilim1 | 19.1754 | 20 | 20.8246 | A | 4.123%
|  | Ilim2 | 0.99978 | 1.5 | 2.0002 | A | 33.35%
|  | UV, rising | 40.5405 | 41.1606 | 41.7808 | V | 1.507%
|  | UV, hyst | 0.88 | 1 | 1.12 | V | 12%
|  | UV, falling | 39.4205 | 40.1606 | 40.9008 | V | 1.843%
|  | OV, rising | 58.8673 | 60.0717 | 61.2762 | V | 2.005%
|  | OV, hyst | 1.232 | 1.4 | 1.568 | V | 12%
|  | OV, falling | 57.2993 | 58.6717 | 60.0442 | V | 2.339%
|  | Ilim, switch | 19.1122 | 20.2 | 21.2878 | V | 5.385%
|  | Inrush Current (with max Cout) | 0.29255 | 0.48 | 0.66745 | A | 39.05%
|  | Time out (Vd =0V) | 1.9286 | 2.25 | 2.5714 | ms | 14.28%
|  | Time out (0.75V<Vd < 1.5V) | 0.96432 | 1.125 | 1.2857 | ms | 14.28%
|  | Time out (Vd > 1.5V) | 0.19286 | 0.225 | 0.25714 | ms | 14.28%
|  | Power Consumption Rcc |  | 71.1504 | 120.7965 | mW
Note: The components calculated in this worksheet are reasonable starting values for a design using the TPS2352x Hot-swap Controller. As such, they are not optimized for any particular performance attribute. See the Instructions tab for additional information.
Consult the TPS2352x datasheet for more detail.
Note on E50: Author: Make sure that this value is higher than Min Recommended Ilim switch.
Note on E51: Inrush Current must be sufficiently below Iin,tmr,min to ensure that timer doesn't run at start-up.
Note on E55: Note that this is an approximation based on the IV characteristics of the CSD19535KTT. This is meant as an initial estimate and should be checked with your actual FET.
Note on E56: Note that this is an approximation based on the IV characteristics of the CSD19535KTT. This is meant as an initial estimate and should be checked with your actual FET.

## BrownOut
ATIS / Brown Out Transient Inputs |  |  | Simplified Diagram
Vin,start | 54 | V
Vin,low | 10 | V
Tdrop | 1 | ms
Vhigh | 54 | V
System Inputs
D1 (Forward Drop) | 1 | V
Cbulk | 0 | mF
Cout | 0.66 | mF
Load During Transient | 1344 | W
Other Losses (Cap ESR, etc) | 1%
HS Gate Recovery time | 0.2 | ms
Ctotal | 0.66 | µF
Typical Ilim | 40 | A
Calculated Values
Vout, min | #NUM! | V
Vds,max | #NUM! | V
Total Recovery Time | #NUM! | ms
Time to D (pin) < 0.75V | #NUM! | ms
Recommended Sesttings
Timer (20% margin) | #NUM! | ms
Ilim,sw (5% margin over Vds,max) | #NUM! | V

## SOA_Checks (hidden)
Teq Calculations
| Using Programmed or target | Programmed
|  | Used for calculations |  |  | Target | Programmed |  | Ilim | 3 | A |  | Assumptions:
| Vds,switch: | 20.2 | V |  | 20 | 20.2 |  | Cgs,FET | 2.4 | nF |  | Ifet = A*Vgst^2
| Iinr | 0.48 | A |  | 0.4 | 0.48 |  | Css,vee,tgt | 118.8 | nF |  | Ifet = Vout / Rshort
| Css | 33 | nF |  | 39.6 | 33 |  | Css,vee,act | 100 | nF
| Css,vee | 100 | nF |  | 118.8 | 100 |  | Css,tgt | 39.6 | nF |  | Css,tot = Cgd,fet + Css_ext
| Time, out (Full) | 2.25 | ms |  | 2 | 2.25 |  | Css,act | 33 | nF |  | Cgs,tot = Cgs,fet + Css,vee
| Ilim, high | 40 | A |  |  |  |  | A | 20 | A/V^2
| Ilim, low | 3 | A
| time, out (medium Vds) | 1.125 | ms |  |  |  |  | use: | Programmed
| time, out, (high Vds) | 0.225 | ms |  |  |  |  | Css,tot | 33 | nF
[8 empty] | Cgs,tot | 100 | nF
[8 empty] | Igate | 20 | uA
| Key Inputs | [6 empty] | Rshort | 1 | ohm
| Vd2 = Max Vin | 60 | V
Start-into Short
| short time-out | 0.225 | ms |  |  |  |  | m | 0.15038 | V/ms
| mid time-out | 1.125 | ms |  |  |  |  | teq1 | 0.85851 | ms
| long time - out | 2.25 | ms |  | Computed | Entered
| teq - hot short | 1.0835 | ms |  | 1.0835 | TBD
| teq - resistive short | 3.5585 | ms |  | 3.5585 | TBD
[8 empty] | Start-into Resistive Short |  |  | Equation: teq,no,cgs = Ilim * Rshort * Css,tot / Igate/2
[8 empty] | teq, no, cgs | 2.475 | ms | <= if FET was ideal and there was no Cgs. Basically just wait until Vout comes up.
[8 empty] | teq,total | 3.3335 | ms | <= As an approximation adding the two computed values seperately
Inrush Current | 0.48
0.58763
0.225 | t1 = Timer
1.0835 | t1' = t1 + Teq hot short
3.5585 | t1'' = t1 + Teq Resistive Short
1.125 | t2 = Max timer at 0.75 <Vd<1.5V
99 | t3 = Vin,max. Time to start with max Iinr | Start-up Time
49.5 | t3' = t3 / 2 (triangular power pulse)
1 | t1'-
10 | t1'+
1 | t1''-
10 | t1''+
1 | t2-
10 | t2+
10 | t3-
100 | t3+
Time (ms) | SOA look up (25C)
1 | Q1 Current handling at 1ms and 60V | 10 | A
10 | Q1 Current handling at 10ms and 60V | 3 | A
1 | Q1 Current handling at 1ms and 60V | 10 | A
10 | Q1 Current handling at 10ms and 60V | 3 | A
10 | Q1 Current handling at 10ms and 60V | 3 | A
100 | Q1 Current handling at 100ms and 60V | 1 | A
1 | Q1 Current handling at 1ms and 20.2V | 10 | A
10 | Q1 Current handling at 10ms and 20.2V | 50 | A
Temp Derating
Time (ms) | Temp Derated SOA (Tj =123C)
| Temp used for derating | 123.4627 | C
| Temp Derating | 0.34358
1 | Q1 Current handling at 1ms and 60V | 3.4358 | A
10 | Q1 Current handling at 10ms and 60V | 1.0307 | A
1 | Q1 Current handling at 1ms and 60V | 3.4358 | A
10 | Q1 Current handling at 10ms and 60V | 1.0307 | A
10 | Q1 Current handling at 10ms and 60V | 1.0307 | A
100 | Q1 Current handling at 100ms and 60V | 0.34358 | A
1 | Q1 Current handling at 1ms and 20.2V | 3.4358 | A
10 | Q1 Current handling at 10ms and 20.2V | 17.1791 | A
W/o Temp derating
Time (ms) | Extrapoloated SOA (Tj =123C) |  |  | m | a
1.0835 | Short Circuit; Vds = 60V, t= 1.08351130840931ms | 3.2947 | A | -0.52288 | 10
3.5585 | Short Circuit with resistor; Vds = 60V, t= 3.55851130840931ms | 1.7692 | A | -0.52288 | 10
49.5 | Start-up ; Vds = 60V, t_eq= 49.5ms | 0.48055 | A | -0.47712 | 9
1.125 | Vd = 1.5V; Vds = 20.2V, t_eq= 1.125ms | 3.7307 | A | 0.69897 | 10
Time (ms) | Operating Point
1.0835 | Short Circuit; Vds = 60V, t= 1.08351130840931ms | 3 | A
3.5585 | Short Circuit with resistor; Vds = 60V, t= 3.55851130840931ms | 3 | A
49.5 | Start-up ; Vds = 60V, t_eq= 49.5ms | 0.48 | A
1.125 | Vd = 1.5V; Vds = 20.2V, t_eq= 1.125ms | 40 | A
SOA Margin (Temp Derated SOA / Req'd SOA)
| Short Circuit; Vds = 60V, t= 1.08351130840931ms | 1.0982
| Short Circuit with resistor; Vds = 60V, t= 3.55851130840931ms | 0.58974
| Start-up ; Vds = 60V, t_eq= 49.5ms | 1.0012
| Vd = 1.5V; Vds = 20.2V, t_eq= 1.125ms | 0.093266

## Error_Calculation (hidden)
| RMS |  |  | Vsns,cl1 | 40
Worst Case
Programmed Settings (Worst Case) | Min | Typ | Max |  | Error | IC parameters
Ilim1 | 19 | 20 | 21 | A | 5% |  | Min | Typ | Max | Units | Errror %
Ilim2 | 0.985 | 1.5 | 2.015 | A | 34.33% | UV, rising | 0.985 | 1 | 1.015 | V | 1.5%
UV, rising | 40.4609 | 41.1606 | 41.8604 | V | 1.7% | OV, rising | 0.98 | 1 | 1.02 | V | 2%
UV, hyst | 0.879 | 1 | 1.121 | V | 12.1% | Iuv | 9 | 10 | 11.2 | uA | 12%
UV, falling | 39.3399 | 40.1606 | 40.9814 | V | NA | Iov | 9 | 10 | 11.2 | uA | 12%
OV, rising | 58.7502 | 60.0717 | 61.3933 | V | 2.2% | Vtmr1 | 1.47 | 1.5 | 1.53 | V | 2%
OV, hyst | 1.2306 | 1.4 | 1.5694 | V | 12.1% | Vtmr2 | 0.735 | 0.75 | 0.765 | V | 2%
OV, falling | 57.1808 | 58.6717 | 60.1627 | V | NA | Vsns, tmr1 | 1.5
Ilim, switch | 18.786 | 20.2 | 21.614 | V | 7% | Itmr1 | 9 | 10 | 11 | uA | 10%
Inrush Current (with max Cout) | 0.216 | 0.48 | 0.744 | A | 55% | Itmr2 | 45 | 50 | 55 | uA | 10%
Time out (Vd =0V) | 1.755 | 2.25 | 2.745 | ms | 22% | Vd | 1.47 | 1.5 | 1.53 | V | 2%
Time out (0.75V<Vd < 1.5V) | 0.8775 | 1.125 | 1.3725 | ms | 22% | Rd | 28.5 | 30 | 31.5 | kΩ | 5%
Time out (Vd > 1.5V) | 0.1755 | 0.225 | 0.2745 | ms | 22%
Programmed Settings (RMS, error) | Min | Typ | Max |  | Error | Vsns,cl2 | 2 | 3 | 4 | mV | 33.33%
Ilim1 | 19.1754 | 20 | 20.8246 | A | 4.123% | Vsns,cl1 | 24 | 25 | 26 | mV | 4%
Ilim2 | 0.99978 | 1.5 | 2.0002 | A | 33.35% | Vsns,cl1 | 38.4 | 40 | 41.6 | mV | 4%
UV, rising | 40.5405 | 41.1606 | 41.7808 | V | 1.507% | Igate,src,low | 15 | 20 | 25 | uA | 25%
UV, hyst | 0.88 | 1 | 1.12 | V | 12% | Igate,src,high |  | 400 |  | uA
UV, falling | 39.4205 | 40.1606 | 40.9008 | V | NA
OV, rising | 58.8673 | 60.0717 | 61.2762 | V | 2.005% | Iq |  |  | 1.1 | mA
OV, hyst | 1.232 | 1.4 | 1.568 | V | 12% | VCC operating | 10 | 14.5
OV, falling | 57.2993 | 58.6717 | 60.0442 | V | NA
Ilim, switch | 19.1122 | 20.2 | 21.2878 | V | 5.385% | [6 empty] | 17.4242
Inrush Current (with max Cout) | 0.29255 | 0.48 | 0.66745 | A | 39.05% | Rshort |  |  | 1 | ohm
Time out (Vd =0V) | 1.9286 | 2.25 | 2.5714 | ms | 14.28%
Time out (0.75V<Vd < 1.5V) | 0.96432 | 1.125 | 1.2857 | ms | 14.28%
Time out (Vd > 1.5V) | 0.19286 | 0.225 | 0.25714 | ms | 14.28%

## T_eq_work_Derivations (hidden)
Discretizing Solution for Sanity Checks
| A | 20 | A/V^2
| Css,tot | 30 | nF
| Cgs,tot | 130 | nF
| Igate | 20 | uA
| Ilim | 1.5 | A
| Rshort | 1 | ohm
| Vin | 60 | V
m | time | Ifet | RTN-VOUTM | Vgst | Qss | Qenh | Qtot | Vds | PFET | deltaE (mJ)
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0
0.1245 | 0.6024 | 0.075 | 0.075 | 0.061237 | 2.25 | 9.798 | 12.048 | 59.925 | 4.4944 | 1.3537
0.23778 | 0.91782 | 0.15 | 0.15 | 0.086603 | 4.5 | 13.8564 | 18.3564 | 59.85 | 8.9775 | 2.1247
0.27963 | 1.186 | 0.225 | 0.225 | 0.10607 | 6.75 | 16.9706 | 23.7206 | 59.775 | 13.4494 | 3.0075
0.30767 | 1.4298 | 0.3 | 0.3 | 0.12247 | 9 | 19.5959 | 28.5959 | 59.7 | 17.91 | 3.8222
0.32873 | 1.6579 | 0.375 | 0.375 | 0.13693 | 11.25 | 21.9089 | 33.1589 | 59.625 | 22.3594 | 4.5937
0.34553 | 1.875 | 0.45 | 0.45 | 0.15 | 13.5 | 24 | 37.5 | 59.55 | 26.7975 | 5.3349
0.35946 | 2.0836 | 0.525 | 0.525 | 0.16202 | 15.75 | 25.923 | 41.673 | 59.475 | 31.2244 | 6.0531
0.3713 | 2.2856 | 0.6 | 0.6 | 0.17321 | 18 | 27.7128 | 45.7128 | 59.4 | 35.64 | 6.7531
0.38158 | 2.4822 | 0.675 | 0.675 | 0.18371 | 20.25 | 29.3939 | 49.6439 | 59.325 | 40.0444 | 7.438
0.39063 | 2.6742 | 0.75 | 0.75 | 0.19365 | 22.5 | 30.9839 | 53.4839 | 59.25 | 44.4375 | 8.1102
0.39869 | 2.8623 | 0.825 | 0.825 | 0.2031 | 24.75 | 32.4962 | 57.2462 | 59.175 | 48.8194 | 8.7715
0.40596 | 3.0471 | 0.9 | 0.9 | 0.21213 | 27 | 33.9411 | 60.9411 | 59.1 | 53.19 | 9.423
0.41255 | 3.2289 | 0.975 | 0.975 | 0.22079 | 29.25 | 35.327 | 64.577 | 59.025 | 57.5494 | 10.066
0.41858 | 3.408 | 1.05 | 1.05 | 0.22913 | 31.5 | 36.6606 | 68.1606 | 58.95 | 61.8975 | 10.7011
0.42412 | 3.5849 | 1.125 | 1.125 | 0.23717 | 33.75 | 37.9473 | 71.6973 | 58.875 | 66.2344 | 11.3292
0.42925 | 3.7596 | 1.2 | 1.2 | 0.24495 | 36 | 39.1918 | 75.1918 | 58.8 | 70.56 | 11.9507
0.434 | 3.9324 | 1.275 | 1.275 | 0.25249 | 38.25 | 40.398 | 78.648 | 58.725 | 74.8744 | 12.5662
0.43844 | 4.1035 | 1.35 | 1.35 | 0.25981 | 40.5 | 41.5692 | 82.0692 | 58.65 | 79.1775 | 13.1761
0.4426 | 4.2729 | 1.425 | 1.425 | 0.26693 | 42.75 | 42.7083 | 85.4583 | 58.575 | 83.4694 | 13.7806
0.4465 | 4.4409 | 1.5 | 1.5 | 0.27386 | 45 | 43.8178 | 88.8178 | 58.5 | 87.75 | 14.3803
[9 empty] | Energy | 164.7357 | mJ
[9 empty] | teq | 1.8304 | ms

## Graphs (hidden)
Vin,max | 60 | V
Cout,max | 792 | uF
I,inr | 0.48 | A | <= At max Cout
Time (ms) | Iin | Vds | Pfet (W) | Pfet,eq
0 | 0 | 60 | 0 | 0
10 | 0 | 60 | 0 | 0
10.01 | 0.48 | 60 | 28.8 | 28.8
59.51 | 0.48 | 30 | 14.4 | 28.8
59.52 | 0.48 | 30 | 14.4 | 0
109.01 | 0.48 | 0 | 0 | 0
109.02 | 0 | 0 | 0 | 0
119.02 | 0 | 0 | 0 | 0
|  | Vds | Ilim
|  | 1 | 40
|  | 20.2 | 40
|  | 20.21 | 3
|  | 100 | 3

## ATIS_Calculations (hidden)
| A | 0.0165 | mF/A = ms/V | <=C/Ilim
| B | 33.6 | V | <= Pload / Ilim
| Trecharge | #NUM! | ms | <= A* (Vhigh - Vend)+A*B*ln[(Vhigh-B)/(Vend-B)]
| Vhalf | #NUM! | V
| Trecharge (1/2) | #NUM! | ms
| Time (ms) | Vin(V) | Vout (V) | I_FET (A) | I_load (A)
| 0 | 54 | 54 | 24.8889 | 24.8889
| 2.5 | 54 | 54 | 24.8889 | 24.8889
Start Drop Out => | 2.51 | 10 | 54 | 0 | 24.8889
| 2.76 | 10 | 43.4469 | 0 | 30.9343 | Note: Adjusting for diode just once.
| 3.01 | 10 | 29.3134 | 0 | 45.8494
| 3.26 | 10 | #NUM! | #NUM! | #NUM!
Finish Drop Out => | 3.51 | 10 | #NUM! | #NUM! | #NUM!
Spike => | 3.511 | 54 | #NUM! | 0 | #NUM!
HS => Recovered | 3.711 | 54 | #NUM! | #NUM! | #NUM!
| #NUM! | 54 | #NUM! | #NUM! | #NUM!
| #NUM! | 54 | #NUM! | #NUM! | #NUM!
Finish Recovery => | #NUM! | 54 | #NUM! | #NUM! | #NUM!
| #NUM! | 54 | 54 | 24.8889 | 24.8889
| #NUM! | 54 | 54 | 24.8889 | 24.8889