## Sheet1
|  | Comments | Recommendation | Status
TEST.PD.PHY.ALL.05 | The total BIST message must have been 13362. 26724 BIST message detected. | Not sure what this is even checking. Seems to be a multiple of 2? Ask if a tester issue. |  | Tester Issue Resolved
TEST.PD.PROT.SRC.08 VCONN Swap | The UUT did not send a Hard Reset signal after the max of tVCONNSourceOn in the PD2 mode. | tVCONN Source on = 50ms Need to check on EVM, seeing 188ms in customer lgos | Tested on our end, did not see this issue. Please retest | Jeff: We have get the customer board, we can ship one board to you for clarify the issue. Please send me your shipping address.
TEST.PD.PS.SRC.01 | The UUT VBUS voltage was not within the limits of vSrcNew or vPpsNew or vAvsNew. | Is PP5V being powered during this time? Does the PD have power?Please share schematic. | Waiting customer response | Jeff: Should be yes. How do I know PP5V powered in this time? I mean how to test this function? Is it source PDO1 5V/3A power? I've passed shcematic via E2E.
TEST.PD.PS.SNK.01 |  | Need to retest, For some reason it is requesting .75 for 20-V instead of 1-A | The customer has "Autonegotiate Sink 0x37", Auto Compute Sink Min Power set to Host controlled. Why did they set this? It seems to affect this test. To fix this test, set this field to "PD Controller will compute" After I changed this, test still failed, but now seems to be a tester issue. Says that PDO not in VIF, but 20-V/1-A is in the VIF | Jeff:Here is the comment from Raymond. 2. For TEST.PD.PS.SRC.03, if the test fails again you can try updating the JSON configuration in Autonegotiate Sink register (0x37) to configure TPS25751 to automatically disable PPHV if the source/tester isn’t able to provide a certain power threshold (Capability mismatch). You’ll need to set these settings below: a. No Capability Mismatch [3] set to 0x0 (The capability mismatch bit will be asserted to indicate to the attached source that more power is desired) b. Auto Disable Sink Upon Capability Mismatch [6] set to 0x1 (enabled) c. Auto Neg Capabilities Mismatch Power [61:52] set to low power (i.e. 250mW).
COMMON.CHECK.PD.3 -TEST.PD.PHY.PORT.1 -Test.PD.PS.SNK.2 | The UUT did not respond to the Tester message with a right GoodCRC. | Need to check in lab Replicated, debugging
COMMON.CHECK.PD.5 -TEST.PD.PS.SNK.2 -Test.pd.ps.src.5 -Test.pd.prot.src.10 | The UUT was not allowed to send Hard_Reset signal./The UUT unexpectedly performs an Error Recovery. | Need to check in lab Replicated, debugging
COMMON.CHECK.PD.7 | In a Fixed PDO in a Source Capabilities message, bits B21:B20 (Peak Power) did not match the vendor value. | Peak Current in VIF and .json don't match. | VIF: PD Source->Source PDOs 2 and 3 JSON: Transmit Source Capabilities PDO 2 and 3 Decide which peak current setting you want for these PDOs, make sure it matches in VIF and JSON | Jeff: I've modified it and make it match.
COMMON.CHECK.PD.12.1 | In a Fixed PDO in the Sink Capabilities message, the current represented by bits B9:B0 did not match the vendor value. | PDO2 current does not match between VIF and JSON | VIF: PD Sink->Sink PDO 2 current is 2200mA JSON: transmit Sink Capabilities-> Sink_PDO2 current is 2.22-A (2220mA) Determine which you want and modify the VIF/JSON appropriately, make sure they match. | Jeff: I've modified it and make it match.
COMMON.CHECK.PD.14 -Test.pd.ps.snk.2 |  | Checking with team
COMMON.PROC.PD.7 | The UUT should have not sent a Discover Identity/SVIDs Request message when Attempts_Discov_SOP = NO. | Does the customer want to support this bit? If yes, just enable in VIF (PD capabilities) Customer: What is this for? TI: When we are a DFP, we can send a discover ID message. It's mainly if they are doing data and alt modes, or want VID/PID info from a far end device. If they don't need any of this (which is likely the case), I can try disabling it. If they want it, they need to change the "Attempts_DISCOV_SOP" VIF field. | Waiting customer response | Jeff: I've modified VIF Attempts_Discov_SOP = YES.