## Instructions
© 2015
LM25066/A/I/AI Design Tool- Rev. D
Typical design procedure
Typical applications require multiple passes through the design tool using MOSFET factors such as transient
thermal response and safe operating area curves. Refer to the following application reports for more detail.
Robust Hot Swap Design
LM25066 Datasheet (See "Design-In Procedure")
The basic design process follows:
1. Enter operating conditions.
2. Select current limit parameters.
3. Enter MOSTFET SOA characteristics & power limit.
4. Select start up conditions (load and/or soft start). Check whether FET is operating with reasonable margin, within the SOA curve.
If not, try changing start-up conditions (soft start values, timer values), add more FETs in parallel, or switch to FET with better SOA.
5. Enter desired UVLO and OVLO values to get recommended resistor values.
6. Done
Notes
1. This worksheet is designed for use with Microsoft Excel 5.0 or later. Its use is intended to assist power supply designers in their
routine, day-to-day calculations.
2. All worksheets have light green inputs cells, white calculated cells, yellow warning cells and red high-risk cells.
3. Formulas and device constants used in the spreadsheet are locked to prohibit them from accidentally being overwritten or deleted.
TEXAS INSTRUMENTS TEXT FILE LICENSE Copyright (c) 2014 Texas Instruments Incorporated All rights reserved not granted herein. Limited License. Texas Instruments Incorporated grants a world-wide, royalty-free, non-exclusive license under copyrights and patents it now or hereafter owns or controls to make, have made, use, import, offer to sell and sell ("Utilize") this software subject to the terms herein. With respect to the foregoing patent license, such license is granted solely to the extent that any such patent is necessary to Utilize the software alone. The patent license shall not apply to any combinations which include this software, other than combinations with devices manufactured by or for TI (“TI Devices”). No hardware patent is licensed hereunder. Redistributions must preserve existing copyright notices and reproduce this license (including the above copyright notice and the disclaimer and (if applicable) source code license limitations below) in the documentation and/or other materials provided with the distribution Redistribution and use in binary form, without modification, are permitted provided that the following conditions are met: * No reverse engineering, decompilation, or disassembly of this software is permitted with respect to any software provided in binary form. * any redistribution and use are licensed by TI for use only with TI Devices. * Nothing shall obligate TI to provide you with source code for the software licensed and provided to you in object code. If software source code is provided to you, modification and redistribution of the source code are permitted provided that the following conditions are met: * any redistribution and use of the source code, including any resulting derivative works, are licensed by TI for use only with TI Devices. * any redistribution and use of any object code compiled from the source code and any resulting derivative works, are licensed by TI for use only with TI Devices. Neither the name of Texas Instruments Incorporated nor the names of its suppliers may be used to endorse or promote products derived from this software without specific prior written permission. DISCLAIMER. THIS SOFTWARE IS PROVIDED BY TI AND TI’S LICENSORS "AS IS" AND ANY EXPRESS OR IMPLIED WARRANTIES, INCLUDING, BUT NOT LIMITED TO, THE IMPLIED WARRANTIES OF MERCHANTABILITY AND FITNESS FOR A PARTICULAR PURPOSE ARE DISCLAIMED. IN NO EVENT SHALL TI AND TI’S LICENSORS BE LIABLE FOR ANY DIRECT, INDIRECT, INCIDENTAL, SPECIAL, EXEMPLARY, OR CONSEQUENTIAL DAMAGES (INCLUDING, BUT NOT LIMITED TO, PROCUREMENT OF SUBSTITUTE GOODS OR SERVICES; LOSS OF USE, DATA, OR PROFITS; OR BUSINESS INTERRUPTION) HOWEVER CAUSED AND ON ANY THEORY OF LIABILITY, WHETHER IN CONTRACT, STRICT LIABILITY, OR TORT (INCLUDING NEGLIGENCE OR OTHERWISE) ARISING IN ANY WAY OUT OF THE USE OF THIS SOFTWARE, EVEN IF ADVISED OF THE POSSIBILITY OF SUCH DAMAGE.

## Design Calculator
LM25066/I/A/IA PMBus Hot Swap Design Tool
www.ti.com/hotswap
Enter Values in Green Shaded Cells
Calculated Values are shown in White Cells
Yellow and Red cells highlight pottential issues with the design. Red highlights items that are higher risk.
| Step 0: Calculator Tutorials |  | Note: Before proceeding, please watch the video tutorials listed to ensure accurate results from this tool!
|  |  | Steps 1 & 2: Operating Conditions, Current Limit, & Circuit Breaker (7:41) | [9 empty] | Yes
|  |  | Step 3: MOSFET Selection (9:58) | [9 empty] | No
Step 4: Startup (10:32)
Step 5: UVLO, OVLO & PGD Thresholds (4:20)
LM25066 Datasheet
|  |  | I understand and agree to watch the video tutorials if help is needed. (Choose Yes to enable the calculator.) |  |  | Yes
|  |  | Assure to follow the layout and application guidelines listed on the datasheet. |  |  | Yes
*For additional questions not addressed in the videos, please post on E2E.ti.com
| Step 1: Operating Conditions |  |  | Minimum Input Operating Voltage: VIN(MIN) | 11 | V
|  |  |  | Nominal Input Operating Voltage: VIN(NOM) | 12 | V
|  |  |  | Maximum Input Operating Voltage: VIN(MAX) | 13 | V
|  |  |  | Maximum Load Current: IOUT(MAX) | 6.5 | A
|  |  |  | Maximum Output Load Capacitance: CLOAD | 100 | µF
|  |  |  | Maximum Ambient Operating Temperature: TMAX | 70 | oC
Steps 1 & 2: Operating Conditions, Current Limit, & Circuit Breaker
| Step 2: Current Limit and Circuit Breaker |  |  | Current Limit Range (CL) | 25 mV | [5 empty] | 25 mV
|  |  |  | Maximum Recommended Value for Effective Sense Resistance | 3.5034 | mW |  |  |  |  | 46 mV
|  |  |  | Use External Resistor Divider to Reduce Effecitve RS | No | [5 empty] | Yes
|  |  |  | Enter the Resistance for RS | 1.5 | mW |  |  |  |  | No
|  |  |  | Recommended Value for RCL1 | NA | W
|  |  |  | Recommended Value for RCL2 | NA | W
| Steps 1 & 2: Operating Conditions, Current Limit, & Circuit Breaker |  |  | Enter value for RCL1 |  | W |  |  |  |  | TRUE
|  |  |  | Enter value for RCL2 |  | W
|  |  |  | Effective Sense Resistance (RS,EFF) | 1.5 | mW
|  |  |  | Resulting Minimum Current Limit | 15.3333 | A
|  |  |  | Resulting Typical Current Limit | 16.6667 | A
|  |  |  | Resulting Maximum Current Limit | 18 | A |  |  |  |  | Retry
|  |  |  | Maximum Power Dissipation in RS | 0.486 | W |  |  |  |  | Latch Off
|  |  |  | Fault Response | Retry | [5 empty] | 1.8 x Current Limit
|  |  |  | Circuit Breaker to Current Limit Raitio | 1.8 x Current Limit | [5 empty] | 3.6 x Current Limit
| Step 3: MOSFET Selection |  |  | Q1 FET Name | PSMN3R7-100BSEJ
|  |  |  | Estimated MOSFET RQJA | 30 | oC/W |  |  |  |  | 10.8025 | 3.5
|  |  |  | Number of MosFETs | 1 | # |  |  |  |  | Values Used
|  |  |  | MOSFET On resistance @ TJ,DC | 4 | mW |  |  |  |  | 4
|  |  |  | Maximum FET Junction Temperature | 175 | oC |  |  |  |  | 175
|  |  |  | 100ms SOA Current (re-use 1ms data if unavailable) @ VIN(MAX) | 300 | A |  |  |  |  | 300
|  |  |  | 1ms SOA Current @ VIN(MAX) | 80 | A |  |  |  |  | 80
| Step 3: MOSFET Selection |  |  | 10ms SOA Current @ VIN(MAX) | 30 | A |  |  |  |  | 30
|  |  |  | 100ms Current at @ VIN(MAX) (use DC if 100ms not available) | 20 | A |  |  |  |  | 20
|  |  |  | 1s or DC SOA Current at @ VIN(MAX) (use DC if 1s not available) | 10 | A |  |  |  |  | 10
| Note: TI recommends choosing a FET with SOA current specified for 100ms and/or 1s or DC. If choosing a FET without these parameters, this calculator will estimate the values via extrapolation, which leaves an inherent associated risk. |  |  | FET Power dissapation at full load (per FET) | 0.169 | W
|  |  |  | Maximum steady state FET Junction Temperature (TJ,DC) | 75.07 | oC
|  |  |  | Minimum Power Limit to Ensure Vsns > 4mV (PLIM,MIN) | 34.6667 | W
|  |  |  | Target Power Limit | 70 | W
|  |  |  | Calculated RPWR | 15.0738 | kW
|  |  |  | Actual RPWR | 49.9 | kW
|  |  |  | Actual PLIM | 189.6777 | W | Note: Hover here to see the 3 values affecting this curve, consult a thermal expert if you are unsure!
| Step 4: Startup |  |  | Load Turn-On Threshold | 12 | V
|  |  |  | Startup Load Type | Constant Current
|  |  |  | Startup Load Value | 6 | A |  |  |  |  | Constant Current
|  |  |  | Use External Soft-Start Control | No | [5 empty] | Resistive
|  |  |  | Typical Start Time with Vinmax (Tstart) | 0.082502 | ms
|  |  |  | IFET - ILOAD margin (lowest for Vout range) | 64%
|  |  |  | Target Fault Timer: Tstart + Margin | 0.14438 | ms
|  |  |  | Target Timer capacitance | 7.6436 | nF
|  |  |  | Selected Timer capacitance | 100 | nF
| Step 4: Startup |  |  | Final Fault Timer(Tfault) | 1.8889 | ms
|  |  |  | Derated SOA / PLIM | 2.7859
|  |  |  | Can a "hot" board be hotplugged | Yes
|  |  |  | Recommended slew Rate (max) | 13.6624 | V/ms
|  |  |  | Recommended slew Rate (min) | 0.052699 | V/ms
| Note: This is the typical dv/dt rate, but max value can be larger. This is because the gate source current can vary from 16uA to 28uA. Thus TI recommends keeping the overall SOA margin during start-up >1.5 in order to compensate for this. |  |  | dv/dt rate on Vout | 4 | V/ms
|  |  |  | calculated SS capacitance | 5.5 | nF
|  |  |  | actual SS capacitance | 10 | nF
|  |  |  | actual dv/dt rate on Vout | 2.2 | V/ms
|  |  |  | SOA margin during start-up | 21.8624
|  |  |  | Target Fault Time | 5 | ms
|  |  |  | Calculated Timer Capacitance | 264.7059 | nF
|  |  |  | Actual Timer Capacitance (pick one smaller than CT,CALC) | 100 | nF
|  |  |  | Actual Fault Time (Tfault) | 1.8889 | ms
|  |  |  | SOA margin during "hot-short" or "start-into short" | 2.7859
|  |  |  | Resulting Typical Insertion Delay Time | 30.9091 | ms
|  |  |  | Resulting Typical Restart Time | 230.4444 | ms
| Step 5: UVLO, OVLO & PGD Thresholds |  |  | Select Option A or Option B | Option A | [5 empty] | Option A
|  |  |  | Desired Upper UVLO Threshold | 11 | V |  |  |  |  | Option B
|  |  |  | Desired Lower UVLO Threshold | 10.5 | V
|  |  |  | Desired Upper OVLO Threshold | 13.5 | V
|  |  |  | Desired Lower OVLO Threshold | 14 | V
|  |  |  | Recommended Resistance for: R1 | 21.7391 | kW
|  |  |  | R2 | 0.59999 | kW
| Step 5: UVLO, OVLO & PGD Thresholds |  |  | R3 | 2.0999 | kW
|  |  |  | R4 | 0 | kW
|  |  |  | Enter the Resistance for R1 | 22 | kW
|  |  |  | Enter the Resistance for R2 | 0.806 | kW
|  |  |  | Enter the Resistance for R3 | 2 | kW
|  |  |  | Enter the Resistance for R4 | 3.65 | kW
|  | Resulting Thresholds: | Minimum | Typical | Maximum
|  | Resulting Upper UVLO Threshold = | 10.5359 | 10.7608 | 10.9857 | V
|  | Resulting Lower UVLO Threshold = | 10.1399 | 10.2548 | 10.3697 | V
|  | Resulting Upper OVLO Threshold = | 14.1518 | 14.3875 | 14.6976 | V
|  | Resulting Lower OVLO Threshold = | 13.5247 | 13.8629 | 14.287 | V
If any of the above cells is red, see the Instrunctions Worksheet
|  |  |  | Enter the Resistance for RPG | 100 | kW
|  |  |  | Desired PGD Rising Threshold | 11.5 | V
|  |  |  | Desired PGD Hysteresis | 0.3 | V
|  |  |  | Recommended Resistance for: RFB1 | 12.5 | kW
|  |  |  | RFB2 | 1.4117 | kW
|  |  |  | Enter Resistance for: RFB1 | 12.4 | kW
|  |  |  | RFB2 | 1.4 | kW
|  |  |  | Nominal PGD Rising Threhold | 11.5033 | V
|  |  |  | Nominal PGD Hysteresis | 297.6 | mV
| Design Summary |  |  | RS = | 1.5 | mW
|  |  |  | RCL1 = | Open | W
|  |  |  | RCL2 = | 0 | W
|  |  |  | RPWR = | 49.9 | kW |  |  | Typical | Units
|  |  |  | CT = | 100 | nF |  | Current limit | 16.6667 | A
|  |  |  | R1 = | 22 | kW |  | Power Limit | 189.6777 | W
|  |  |  | R2 = | 0.806 | kW |  | Circuit Breaker Current | 30 | A
|  |  |  | R3 = | 2 | kW |  | Startup Time | 0.082502 | ms
|  |  |  | R4 = | N/A | kW |  | Insertion Delay | 30.9091 | ms
|  |  |  | RFB1 = | 12.4 | kW |  | Fault Timeout | 1.8889 | ms
|  |  |  | RFB2 = | 1.4 | kW |  | Restart Time During Fault | 230.4444 | ms
|  |  |  | RPG = | 100 | kW |  | Upper UVLO Threshold | 10.7608 | V
|  |  |  | CIN = | 0.01 | µF |  | Lower UVLO Threshold | 10.2548 | V
|  |  |  | CVDD = | 1 | µF |  | Upper OVLO Threshold | 14.3875 | V
|  |  |  | CVREF = | 1 | µF |  | Lower OVLO Threshold | 13.8629 | V
|  |  |  | D1, D3 = | 1N4148W-7-F |  |  | PGD Threshold | 11.5033 | V
|  |  |  | D2 = | SK153-TP
|  |  |  | Cdv/dt = | DNP | nF |  | PGD Hystersis | 297.6 | mV
|  |  |  | Connect CL Pin to | GND | µF
|  |  |  | Connect CB Pin to | GND | µF
|  |  |  | Connect /Retry to | GND | µF
|  |  |  | Q1 = | PSMN3R7-100BSEJ
|  |  |  | Q2 = | MMBT3904
|  |  |  | Q3 = | MMBT3906
|  |  |  | Z1 = | 5.0SMDJXXX
| Notes: | 1. Although not mandatory, CIN provides transient suppression at the VIN pin
2. A TVS clamp from VIN to GND is absolutely mandatory to clamp the voltage overshoot upon MOSFET turn-off, e.g. during circuit breaker
3. Componet tolerances not accounted for in Min/Max Calculations.
Note: The components calculated in this worksheet are reasonable starting values for a design using the LM25066/I PMBus Hot-swap Controller. As such, they are not optimized for any particular performance attribute. Tolerances of the components are not included in the calculations. See the Instructions tab for additional information.
Consult the LM25066/I datasheet for more detail.
Max RS = 45 mV
(Max Load Current x 1.01)
The 1.01 factor provides 1% margin from the max. normal load current.
RCL1
RCL2
Note on F27: The minimum system voltage must be no less than 2.9V.
Note on F29: The maximum system voltage must be no greater than 17V.
Note on F31: This is the capacitance at Vout. This should not be zero. A minimum of 10 μF is recommended.
Note on F37: Select either 25mV or 46mV current limit. 25mV will result in less power loss in the Rs resistor.
Note on F39: Using an External Resistor allows the user to fine tune the current limit for a given standard resistor. It will add error to the power limit, current limit, and telemetry (1% resistors) and should be avoided if possible.
Note on F40: When using an external resistor divider, Rs must be larger than the targeted Rs,eff. Pick the next larger available Rs. When not using an external resistor divider, pick the next smallest available sense resistor.
Note on F41: Cell turns Red if When using an external resistor divider, Rs must be larger than the targeted Rs,eff. Pick the next larger available Rs.
Note on F46: Ensure that the minimum current limit is above maximum load.
Note on F47: Ensure that the minimum current limit is above maximum load.
Note on F48: Ensure that the minimum current limit is above maximum load.
Note on F49: The power dissipation is calculated using the maximum normal load current. Ensure the selected resistor is rated for this power dissipation.
Note on F53: Note that this parameter is heavily dependent on the board layout and amount of copper connected to the Drain of the FET. The TI EVM is ~30C / W number and is a good starting point. It's recommended to measure this value again once the boards are built and plugging this back into the calculator.
Note on F63: If FET temperature is too high, increase the # of FETs, reduce the load, or reduce the RθJA by adding more heat sinking to MOSFETs.
Note on F65: Usually this can be set to PLIM,MIN. If a load is present during start-up a higher Plim, may be preferred.
Note on F68: Cell turns Red if the actual power limit is below Minimum Power Limit (cell F46)
Note on I68: 3 Parameters: Step 1: Max Ambrient Operating Temperature Step 3: Estimated MOSFET RQJA Step 3: FET Power Dissipation at full load **This includes air flow
Note on F70: Select if the load will draw current during start-up. For no Load, choose constant current and set to zero
Note on F72: Yes or No. Default is No. However, DV/DT control can be useful in high current applications or applications were COUT is large. If SOA margin is poor with a PLIM start-up, switching to a soft start can alleviate this problem.
Note on F74: If IFET - ILOAD margin is too low, there may be start-up issues due to variation in power limit or load profile. A margin > 25% is recommended. If margin is < 25%, the power limit should be increased or the load should be kept completely OFF during start-up.
Note on F75: TO ensure start-up the faul time out must be longer than the start-up time. It is recommended to choose a fault timer that is larger than the typical start-time to account for variations in Plim, timer current, and timer capacitance.
Note on F77: Pick closest capacitor that is larger than the Target capacitance
Note on F79: A ratio over 1.1 is required and over 1.3 is preferred. This will account for variation in Power limit and timer If the margin is poor with a PLIM based start-up, reduce timer, reduce power limit, use more FETs in parallel or switch to soft start (cell F55)
Note on F80: This is used to determine the maximum FET case temperature before start-up. A "yes" here means that a user may run a board at full current, then unplug the board and plug it back in. In that the FET is hot before hot-plug. If this is a "no". FET temperature just equals the ambient temperature.
Note on F81: If these cells are red, there is no suitable slew rate for keeping FET whithin SOA. Reduce load at start-up or pick FET with better SOA.
Note on F82: If these cells are red, there is no suitable slew rate for keeping FET whithin SOA. Reduce load at start-up or pick FET with better SOA.
Note on F83: Ensure that this is lower than max ss slew rate in the cell above
Note on F86: Ensure that this is lower than max ss slew rate.
Note on F87: A margin of >1.1 is required and a margin of >1.3 is recommended to accout for the variation in the gate current. Reduce dv/dt rate to reduce inrush current and increase SOA margin
Note on F92: A margin of >1.1 is required and a margin of >1.3 is recommended to accout for the variation in the power limit and timer. Reduce Tfault to improve SOA margin.
Note on F94: This calculation applies only when the RETRY option is selected.
Note on F95: See the schematics above to select the appropriate option for setting the input voltage UVLO and OVLO thresholds.
Note on F96: This threshold must be between 2.9V and 17V.
Note on F97: This threshold must be greater than 2.65V, and less than the upper UVLO threshold.
Note on F98: This threshold must be greater than the upper UVLO Threshold, and less than 17V.
Note on F146: TI recommended. Same as EVM
Note on F148: TI recomends the SMDJxx TVS, which are used on the EVM. Pick the proper value based on the input voltage.

## Device Parmaters (hidden)
|  | Min | Typ | Max | Units
Operating Conditions
| Junction Temperature | -40 |  | 125
| Input Voltage | 2.9 |  | 17 | V
Current Limit
| Threshold Voltage CL = GND | 23 | 25 | 27
| Threshold Voltage CL = VDD | 42.3 | 46 | 49.7
| Sense input Current |  | 33 |  | uA
Power Limit
| Systematic Offset |  |  | 0.0021 | V
| Minimum Recommended Vsns |  |  | 0.004 | V | <= I am assuming this would have +/- 50% error at best
| A_coeff |  |  | 194000
| Key Equations: | Vsns = Rpwr / (A*Vds) + Vos,syst | [5 empty] | Example: | Vds | Rpwr | Rsns (m-ohm) | Plim | Vsns (mV) | Plim | Rpwr
|  | Plim (Vds) = 1/Rs * [ Rpwr/A + Vds * Vos, syst] | [6 empty] | 12 | 25 | 0.5 | 308.132 | 0.012839 | 82 | 3065.2
|  | Rpwr = A * [PLIM(Vds) * Rs - Vds*Vos,syst] | [6 empty] | 12 | 5 | 0.5 | 101.9464 | 0.0021499
| How Plim varries vs Vds: | [6 empty] | Ex: Plim @ 13V = 100W, Rs = 0.5; Plim @ (Vds = 5V) = 100W - 7V * 1mV/0.5mili-ohm = 100W - 14W = 86W
Timer
| Upper Threshold | 1.54 | 1.7 | 1.85 | V
| Insertion Time Current | -3 | -5.5 | -8 | uA
timer_constant
| Fault detection current | 120 | 90 | 60 | uA
| Computed Start - Up Slop |  | 0.74613 |  |  | <= mean root square(T_start_error_Plim, timer_error, cap_error); T_start proportional to 1/Plim => T_start_error_plim = 1/(1-Plim_err) - 1 = 1/(1-0.4) - 1 = 0.66
| Slop for calculations |  | 0.75 |  |  | Note: We get additional buffer, b/c this is designed for a Vinmax, while typically Vin = Vinnom
Gate
| Gate Sourcing Current | 16 | 22 | 28
Circuit Breaker
| 1.8 x Threshold | 35 | 45 | 55
| 1.8x CB:CL Ratio | 1.6 | 1.8 | 2
| 3.6 x Threshold | 70 | 90 | 110
| 3.6x CB:CL Ratio | 3.1 | 3.6 | 4
Timer Pin
| Upper Threshold | 1.54 | 1.7 | 1.85
| Lower Threshold (Restart) | 0.85 | 1 | 1.07
| End of Cycle |  | 0.3
| Re-enable threshold |  | 0.3
| Insertion time current | 3 | 5.5 | 8
| Sink current, end of insertion | 1.4 | 1.9 | 2.4
| Fault detection current | 60 | 90 | 120
| Fault sink current |  | 2.8
Power Good
| PGVOL |  | 25 | 60 | mV | 2 | mA sinking
FB Pin
| FB Threshold | 1.141 | 1.167 | 1.19 | V
| FB Hysteresis Current | 18 | 24 | 31 | uA

## Equations (hidden)
Current Limit
|  |  | CLMIN = | 23 | mV
|  |  | CLNOM = | 25 | mV
|  |  | CLMAX = | 27 | mV
|  |  |  | Max Rs = | 3.5034
|  |  |  | RCL1 Recommended = | NA
|  |  |  | RCL2 Recommmended = | NA
|  |  |  | Effective Rs = | 1.5
|  |  |  | Min. Current limit = | 15.3333
|  |  |  | Typ. Current limit = | 16.6667
|  |  |  | Max. Current limit = | 18
|  |  |  | Rs Power Diss. = | 486
FET Selection
[5 empty] | Nominal |  | Derated at TJ
|  |  |  | 100ms SOA Current Maximum Input Voltage | 3900 | W | 2598.18
|  |  |  | 1ms SOA Current Maximum Input Voltage | 1040 | W | 692.848
|  |  |  | 10ms SOA Current Maximum Input Voltage | 390 | W | 259.818
|  |  |  | 100ms or DC SOA Current at Maximum Input Voltage | 260 | W | 173.212
|  |  |  | Minimum Power Limit= | 34.6667 | W
|  |  |  | Target PLIM | 70 | W
|  |  |  | Rpwr | 15.0738 | k-ohm
|  |  |  | Rpwr actual | 49.9 | k-ohm
|  |  |  | Final Plim | 189.6777 | W
|  |  |  | Resulting Typical Power Limit = | 144.155 | 24% tolerance used in this calculation.
|  |  |  | Resulting Minimum Power Limit = | 189.6777
|  |  |  | Resulting Maximum Power Limit = | 235.2003
Startup
With PLIM
|  |  |  | Typical Start time | 0.082502 | ms
|  |  |  | Start-slop | 0.75
|  |  |  | Target Fault Timer | 0.14438 | ms
|  |  |  | Target Timer capacitance | 7.6436 | nF
|  |  |  | Selected Timer capacitance | 100 | nF
|  |  |  | Final Fault Timer | 1.8889 | ms
|  |  |  | SOA / PLIM | 2.7859
With SS
|  |  |  | dv/dt rate | 4 | V/ms
|  |  |  | calculated SS capacitance | 5.5 | nF
|  |  |  | actual SS capacitance | 10 | nF
|  |  |  | actual dv/dt rate | 2.2 | V/ms
|  |  |  | I_Cout | 0.22 | A
|  |  |  | typical start time | 5.9091 | ms
|  |  |  | FET Energy dissipated at start-up (EFET) | 0.0084004 | J
|  |  |  | Peak Power dissipated during start-up (PFET) | 189.6777 | W
|  |  |  | Equivalent time at peak power - EFET/PFET (t_power) | 0.044288 | ms
|  |  |  | Available SOA for t_power at Vinmax | 4146.8057 | W
|  |  |  | SOA margin | 21.8624
[5 empty] | 1 | ms
Covering hot-short, start-into short for SS
|  |  |  | Target Fault Time | 5
|  |  |  | Calculated Timer Capacitance | 264.7059 | nF
|  |  |  | Actual Timer Capacitance | 100 | nF
|  |  |  | Actual Fault Time (Tfault) | 1.8889 | ms
|  |  |  | Available derated SOA for Tfault | 528.4242 | W
|  |  |  | SOA margin | 2.7859
10% margin added in this calculation
[8 empty] | UVLO upper is F40 |  |  | R1 is F48
A
V/S
nF
|  |  |  | Min Insertion time = | 19.25 | ms
|  |  |  | Typ. Insertion time = | 30.9091 | ms
|  |  |  | Max Insertion time = | 61.6667 | ms
|  |  |  | Min Restart time = | 219.5274 | ms | 0.027417 | 1.9714 | 0.19643
|  |  |  | Typ. Restart time = | 230.4444 | ms | 0.054444 | 2 | 0.25
|  |  |  | Max Restart time = | 262.0238 | ms | 0.11667 | 2.2286 | 0.275
|  |  |  | Min PG Threshold = | 11.247
|  |  |  | Nom PG Threshold = | 11.5033
|  |  |  | Max PG Threshold = | 11.73
|  |  |  | Min PG Hysteresis = | 223.2
|  |  |  | Nom PG Hysteresis = | 297.6
|  |  |  | Max PG Hysteresis = | 384.4
[8 empty] | UVLO lower is F41 |  |  | R2 is F49
[8 empty] | OVLO upper is F42 |  |  | R3 is F50
[8 empty] | OVLO lower is F43 |  |  | R4 is F51
Option A
Option B
[5 empty] | A | B
|  |  |  | R1 = | 21.7391 | 21.7391
|  |  |  | R2 = | 0.59999 | 2.6999
|  |  |  | R3 = | 2.0999 | -21.7391
|  |  |  | R4 = |  | -2.0435
|  |  |  | Resulting upper UVLO Threshold (min) = | 10.5359 | 32.8507
|  |  |  | Resulting upper UVLO Threshold (typ) = | 10.7608 | 33.3285
|  |  |  | Resulting upper UVLO Threshold (max) = | 10.9857 | 33.8064
|  |  |  | Resulting lower UVLO Threshold (min) = | 10.1399 | 32.4547
|  |  |  | Resulting lower UVLO Threshold (typ) = | 10.2548 | 32.8225
|  |  |  | Resulting lower UVLO Threshold (max) = | 10.3697 | 33.1904
|  |  |  | Resulting upper OVLO Threshold (min) = | 14.1518 | 1.7662
|  |  |  | Resulting upper OVLO Threshold (typ) = | 14.3875 | 1.7956
|  |  |  | Resulting upper OVLO Threshold (max) = | 14.6976 | 1.8343
|  |  |  | Resulting lower OVLO Threshold (min) = | 13.5247 | 1.7102
|  |  |  | Resulting lower OVLO Threshold (typ) = | 13.8629 | 1.7496
|  |  |  | Resulting lower OVLO Threshold (max) = | 14.287 | 1.7983
|  |  |  | Ramp time for output voltage | #REF! | ms
|  |  |  | Nominal output voltage | 12 | V
|  |  |  | Required soft-start capacitance | #REF! | nF
GRAPH:
|  |  |  | Selected Rs = | 1.5
|  |  |  | Selected RPWR = | 49.9
|  |  |  | Max System voltage = | 13
|  |  |  | Current Lim (min) = | 15.3333
|  |  |  | Current Lim (typ) = | 16.6667
|  |  |  | Current Lim (max) = | 18
|  |  |  | Power Limit (min) = | 144.155
|  |  |  | Power Limit (typ) = | 189.6777
|  |  |  | Power Limit (max) = | 235.2003
|  |  | A) This table calculates the Ids current based |  |  |  |  | B) This table corrrects the table at left so no |  |  |  | C) This table creates the |  |  | D) This table changes ID values to zero for Vds>Vin(max)
|  |  | on power limit only - no current limit info. |  |  |  |  | current is greater than the current limit. |  |  |  | SOA data points from |  |  | and adds the SOA curve. This data is plotted.
| PLIM |  | Vds | Min | Typ | Max |  | Vds | Min | Typ | Max | the customer's SOA |  |  | Vds | Min | Typ | Max | SOA | Temp Derated SOA
| 172.8777 |  | 1 | 129.6582 | 172.8777 | 216.0971 |  | 1 | 15.3333 | 16.6667 | 18 | data he entered. |  |  | 1 | 15.3333 | 16.6667 | 18 | 528.4242 | 528.4242 | W
| 174.2777 |  | 2 | 65.3541 | 87.1388 | 108.9235 |  | 2 | 15.3333 | 16.6667 | 18 |  |  |  | 2 | 15.3333 | 16.6667 | 18 | 264.2121
| 175.6777 |  | 3 | 43.9194 | 58.5592 | 73.199 |  | 3 | 15.3333 | 16.6667 | 18 |  | User's |  | 3 | 15.3333 | 16.6667 | 18 | 176.1414
| 177.0777 |  | 4 | 33.2021 | 44.2694 | 55.3368 |  | 4 | 15.3333 | 16.6667 | 18 | Vds | Ids |  | 4 | 15.3333 | 16.6667 | 18 | 132.106
| 178.4777 |  | 5 | 26.7716 | 35.6955 | 44.6194 |  | 5 | 15.3333 | 16.6667 | 18 | 1 | 528.4242 | x = customer's entry | 5 | 15.3333 | 16.6667 | 18 | 105.6848
| 179.8777 |  | 6 | 22.4847 | 29.9796 | 37.4745 |  | 6 | 15.3333 | 16.6667 | 18 | 2 | 478.0981 |  | 6 | 15.3333 | 16.6667 | 18 | 88.0707
| 181.2777 |  | 7 | 19.4226 | 25.8968 | 32.371 |  | 7 | 15.3333 | 16.6667 | 18 | 3 | 462.3711 |  | 7 | 15.3333 | 16.6667 | 18 | 75.4892
| 182.6777 |  | 8 | 17.126 | 22.8347 | 28.5434 |  | 8 | 15.3333 | 16.6667 | 18 | 4 | 450.1391 |  | 8 | 15.3333 | 16.6667 | 18 | 66.053
| 184.0777 |  | 9 | 15.3398 | 20.4531 | 25.5663 |  | 9 | 15.3333 | 16.6667 | 18 | 5 | 440.3535 | x | 9 | 15.3333 | 16.6667 | 18 | 58.7138
| 185.4777 |  | 10 | 13.9108 | 18.5478 | 23.1847 |  | 10 | 13.9108 | 16.6667 | 18 | 6 | 299.4404 |  | 10 | 13.9108 | 16.6667 | 18 | 52.8424
| 186.8777 |  | 11 | 12.7417 | 16.9889 | 21.2361 |  | 11 | 12.7417 | 16.6667 | 18 | 7 | 198.7881 |  | 11 | 12.7417 | 16.6667 | 18 | 48.0386
| 188.2777 |  | 12 | 11.7674 | 15.6898 | 19.6123 |  | 12 | 11.7674 | 15.6898 | 18 | 8 | 123.299 |  | 12 | 11.7674 | 15.6898 | 18 | 44.0353
| 189.6777 |  | 13 | 10.9429 | 14.5906 | 18.2382 |  | 13 | 10.9429 | 14.5906 | 18 | 9 | 64.5852 |  | 13 | 10.9429 | 14.5906 | 18 | 40.648
| 191.0777 |  | 14 | 10.2363 | 13.6484 | 17.0605 |  | 14 | 10.2363 | 13.6484 | 17.0605 | 10 | 17.6141 | x | 14 | 5e-10 | 5e-10 | 5e-10 | 37.7446
| 192.4777 |  | 15 | 9.6239 | 12.8318 | 16.0398 |  | 15 | 9.6239 | 12.8318 | 16.0398 | 11 | 11.7428 |  | 15 | 5e-10 | 5e-10 | 5e-10 | 35.2283
| 193.8777 |  | 16 | 9.088 | 12.1174 | 15.1467 |  | 16 | 9.088 | 12.1174 | 15.1467 | 12 | 7.5489 |  | 16 | 5e-10 | 5e-10 | 5e-10 | 33.0265
| 195.2777 |  | 17 | 8.6152 | 11.4869 | 14.3587 |  | 17 | 8.6152 | 11.4869 | 14.3587 | 13 | 4.4035 |  | 17 | 5e-10 | 5e-10 | 5e-10 | 31.0838
[12 empty] | 14 | 1.9571 |  | 18 | 5e-10 | 5e-10 | 5e-10 | 29.3569
|  |  | Note: I added an adjustment for the systematic offset | [8 empty] | 15 | 0 | x | 19 | 5e-10 | 5e-10 | 5e-10 | 27.8118
[12 empty] | 16 | 0 |  | 20 | 5e-10 | 5e-10 | 5e-10 | 26.4212
|  |  | Vos syst | 0.0021 | [7 empty] | 17 | 0
|  |  | Rs (ohm) | 0.0015 | [7 empty] | 18 | 0
|  |  | Vin, max | 13 | [7 empty] | 19 | 0
|  |  | Plim tolerance |  | 0.25 | [6 empty] | 20 | 0 | x
Plim (Vds) = Plim (Vin,max) + (Vds - Vin,max)*Vos,syst/Rs
Option A
R1 = UVLO(upper) - UVLO(lower)
23 uA
R3 = 1.16V x R1 x UVLO(lower)
OVLO(upper) x (UVLO(lower) - 1.16V)
R2 = 1.16V x R1 - R3
UVLO(lower) - 1.16V
Typical UVLO(upper) = 1.16V + (R1 x ( 1.16V + 23uA)
(R2 + R3)
Typical UVLO(lower) = 1.16V x (R1 + R2 + R3)
(R2 + R3)
Typical OVLO(upper) = 1.16V x (R1 + R2 + R3)
R3
Typical OVLO(lower) = ((R1 + R2) x (( 1.16V) - 23uA)) + 1.16V
R3
Rpwr = 1.71 x 105 x Rs x PFET
PFET(min) = 4.44 x 10-6 x Rpwr
Rs
PFET(typ) = 5.85 x 10-6 x Rpwr
Rs
PFET(max) = 7.25 x 10-6 x Rpwr
Rs

## Start_up (hidden)
| PLIM | ILIM | Load type |  | SS | Load Value | Load start | Rs | Vos,syst |  |  | Start-time |  | I_fet-I_L margin |  | I_g(hi/nom) | I_g(low/nom)
| 189.6777 | 16.6667 | CC |  | No | 6 | 12 | 1.5 | 0.0021 |  |  | 0.082502 | ms | 64% |  | 1.2727 | 0.72727
|  |  | To avoid timer running: Iload + Icap,ss < IFET_PLIM / 2 => SS_RATE < 1/Cout * (IFET_PLIM/2 - ILOAD) | [8 empty] | Max_SS_Rate | 23.3333 | V/ms | max_power_typ | 189.6777 | W
[12 empty] | FET_ENERGY | 0.0084004 | J | max_power_high | 6.28 | W
[15 empty] | max_power_low | 6.16 | W
VIN | Vout | ILOAD | PLIM | IFET_PLIM | I_FET_SS | IFET | ICAP | Dt | Time | Tiime (ms) | I_Fet-IL margin | Max _allowed SS_rate | FET_Energy | Power (W) | P_ fast_SS | P_slow_SS
[10 empty] | -10 |  |  |  | 0
[10 empty] | -0.01 |  |  |  | 0
13 | 0 | 0 | 189.6777 | 14.5906 | 0.22 | 14.5906 | 14.5906 | 0 | 0 | 0 | 100% | 72.9529 | 0 | 189.6777 | 3.64 | 2.08
13 | 0.125 | 0 | 189.5027 | 14.7187 | 0.22 | 14.7187 | 14.7187 | 8.4926e-07 | 8.4926e-07 | 0.00084926 | 100% | 73.5933 | 0.00016094 | 189.5027 | 3.605 | 2.06
13 | 0.25 | 0 | 189.3277 | 14.8492 | 0.22 | 14.8492 | 14.8492 | 8.4179e-07 | 1.6911e-06 | 0.0016911 | 100% | 74.2461 | 0.00015938 | 189.3277 | 3.57 | 2.04 |  | Start-up slop
13 | 0.375 | 0 | 189.1527 | 14.9824 | 0.22 | 14.9824 | 14.9824 | 8.3431e-07 | 2.5254e-06 | 0.0025254 | 100% | 74.9119 | 0.00015781 | 189.1527 | 3.535 | 2.02 |  | QG | 0.3
13 | 0.5 | 0 | 188.9777 | 15.1182 | 0.22 | 15.1182 | 15.1182 | 8.2682e-07 | 3.3522e-06 | 0.0033522 | 100% | 75.5911 | 0.00015625 | 188.9777 | 3.5 | 2 |  | I_Src | 0.3
13 | 0.625 | 0 | 188.8027 | 15.2568 | 0.22 | 15.2568 | 15.2568 | 8.1931e-07 | 4.1715e-06 | 0.0041715 | 100% | 76.2839 | 0.00015469 | 188.8027 | 3.465 | 1.98 |  | RMS | 0.42426
13 | 0.75 | 0 | 188.6277 | 15.3982 | 0.22 | 15.3982 | 15.3982 | 8.1178e-07 | 4.9833e-06 | 0.0049833 | 100% | 76.9909 | 0.00015312 | 188.6277 | 3.43 | 1.96
13 | 0.875 | 0 | 188.4527 | 15.5425 | 0.22 | 15.5425 | 15.5425 | 8.0425e-07 | 5.7875e-06 | 0.0057875 | 100% | 77.7124 | 0.00015156 | 188.4527 | 3.395 | 1.94 |  | PLIM | 0.3
13 | 1 | 0 | 188.2777 | 15.6898 | 0.22 | 15.6898 | 15.6898 | 7.967e-07 | 6.5842e-06 | 0.0065842 | 100% | 78.449 | 0.00015 | 188.2777 | 3.36 | 1.92 |  | combined | 0.42426
13 | 1.125 | 0 | 188.1027 | 15.8402 | 0.22 | 15.8402 | 15.8402 | 7.8913e-07 | 7.3734e-06 | 0.0073734 | 100% | 79.2011 | 0.00014844 | 188.1027 | 3.325 | 1.9
13 | 1.25 | 0 | 187.9277 | 15.9938 | 0.22 | 15.9938 | 15.9938 | 7.8155e-07 | 8.1549e-06 | 0.0081549 | 100% | 79.9692 | 0.00014688 | 187.9277 | 3.29 | 1.88 |  | I_timer | 0.2
13 | 1.375 | 0 | 187.7527 | 16.1508 | 0.22 | 16.1508 | 16.1508 | 7.7396e-07 | 8.9289e-06 | 0.0089289 | 100% | 80.7538 | 0.00014531 | 187.7527 | 3.255 | 1.86 |  | C_timer | 0.2
13 | 1.5 | 0 | 187.5777 | 16.3111 | 0.22 | 16.3111 | 16.3111 | 7.6635e-07 | 9.6952e-06 | 0.0096952 | 100% | 81.5555 | 0.00014375 | 187.5777 | 3.22 | 1.84 |  | RMS | 0.28284
13 | 1.625 | 0 | 187.4027 | 16.475 | 0.22 | 16.475 | 16.475 | 7.5873e-07 | 1.0454e-05 | 0.010454 | 100% | 82.3748 | 0.00014219 | 187.4027 | 3.185 | 1.82
13 | 1.75 | 0 | 187.2277 | 16.6425 | 0.22 | 16.6425 | 16.6425 | 7.5109e-07 | 1.1205e-05 | 0.011205 | 100% | 83.2123 | 0.00014063 | 187.2277 | 3.15 | 1.8 |  | Final | 0.5099
13 | 1.875 | 0 | 187.0527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 1.1955e-05 | 0.011955 | 100% | 83.3333 | 0.00013906 | 185.4167 | 3.115 | 1.78
13 | 2 | 0 | 186.8777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 1.2705e-05 | 0.012705 | 100% | 83.3333 | 0.0001375 | 183.3333 | 3.08 | 1.76
13 | 2.125 | 0 | 186.7027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 1.3455e-05 | 0.013455 | 100% | 83.3333 | 0.00013594 | 181.25 | 3.045 | 1.74
13 | 2.25 | 0 | 186.5277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 1.4205e-05 | 0.014205 | 100% | 83.3333 | 0.00013438 | 179.1667 | 3.01 | 1.72
13 | 2.375 | 0 | 186.3527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 1.4955e-05 | 0.014955 | 100% | 83.3333 | 0.00013281 | 177.0833 | 2.975 | 1.7
13 | 2.5 | 0 | 186.1777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 1.5705e-05 | 0.015705 | 100% | 83.3333 | 0.00013125 | 175 | 2.94 | 1.68
13 | 2.625 | 0 | 186.0027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 1.6455e-05 | 0.016455 | 100% | 83.3333 | 0.00012969 | 172.9167 | 2.905 | 1.66
13 | 2.75 | 0 | 185.8277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 1.7205e-05 | 0.017205 | 100% | 83.3333 | 0.00012813 | 170.8333 | 2.87 | 1.64
13 | 2.875 | 0 | 185.6527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 1.7955e-05 | 0.017955 | 100% | 83.3333 | 0.00012656 | 168.75 | 2.835 | 1.62
13 | 3 | 0 | 185.4777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 1.8705e-05 | 0.018705 | 100% | 83.3333 | 0.000125 | 166.6667 | 2.8 | 1.6
13 | 3.125 | 0 | 185.3027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 1.9455e-05 | 0.019455 | 100% | 83.3333 | 0.00012344 | 164.5833 | 2.765 | 1.58
13 | 3.25 | 0 | 185.1277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 2.0205e-05 | 0.020205 | 100% | 83.3333 | 0.00012188 | 162.5 | 2.73 | 1.56
13 | 3.375 | 0 | 184.9527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 2.0955e-05 | 0.020955 | 100% | 83.3333 | 0.00012031 | 160.4167 | 2.695 | 1.54
13 | 3.5 | 0 | 184.7777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 2.1705e-05 | 0.021705 | 100% | 83.3333 | 0.00011875 | 158.3333 | 2.66 | 1.52
13 | 3.625 | 0 | 184.6027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 2.2455e-05 | 0.022455 | 100% | 83.3333 | 0.00011719 | 156.25 | 2.625 | 1.5
13 | 3.75 | 0 | 184.4277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 2.3205e-05 | 0.023205 | 100% | 83.3333 | 0.00011562 | 154.1667 | 2.59 | 1.48
13 | 3.875 | 0 | 184.2527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 2.3955e-05 | 0.023955 | 100% | 83.3333 | 0.00011406 | 152.0833 | 2.555 | 1.46
13 | 4 | 0 | 184.0777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 2.4705e-05 | 0.024705 | 100% | 83.3333 | 0.0001125 | 150 | 2.52 | 1.44
13 | 4.125 | 0 | 183.9027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 2.5455e-05 | 0.025455 | 100% | 83.3333 | 0.00011094 | 147.9167 | 2.485 | 1.42
13 | 4.25 | 0 | 183.7277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 2.6205e-05 | 0.026205 | 100% | 83.3333 | 0.00010938 | 145.8333 | 2.45 | 1.4
13 | 4.375 | 0 | 183.5527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 2.6955e-05 | 0.026955 | 100% | 83.3333 | 0.00010781 | 143.75 | 2.415 | 1.38
13 | 4.5 | 0 | 183.3777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 2.7705e-05 | 0.027705 | 100% | 83.3333 | 0.00010625 | 141.6667 | 2.38 | 1.36
13 | 4.625 | 0 | 183.2027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 2.8455e-05 | 0.028455 | 100% | 83.3333 | 0.00010469 | 139.5833 | 2.345 | 1.34
13 | 4.75 | 0 | 183.0277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 2.9205e-05 | 0.029205 | 100% | 83.3333 | 0.00010312 | 137.5 | 2.31 | 1.32
13 | 4.875 | 0 | 182.8527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 2.9955e-05 | 0.029955 | 100% | 83.3333 | 0.00010156 | 135.4167 | 2.275 | 1.3
13 | 5 | 0 | 182.6777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 3.0705e-05 | 0.030705 | 100% | 83.3333 | 0.0001 | 133.3333 | 2.24 | 1.28
13 | 5.125 | 0 | 182.5027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 3.1455e-05 | 0.031455 | 100% | 83.3333 | 9.8438e-05 | 131.25 | 2.205 | 1.26
13 | 5.25 | 0 | 182.3277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 3.2205e-05 | 0.032205 | 100% | 83.3333 | 9.6875e-05 | 129.1667 | 2.17 | 1.24
13 | 5.375 | 0 | 182.1527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 3.2955e-05 | 0.032955 | 100% | 83.3333 | 9.5313e-05 | 127.0833 | 2.135 | 1.22
13 | 5.5 | 0 | 181.9777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 3.3705e-05 | 0.033705 | 100% | 83.3333 | 9.375e-05 | 125 | 2.1 | 1.2
13 | 5.625 | 0 | 181.8027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 3.4455e-05 | 0.034455 | 100% | 83.3333 | 9.2187e-05 | 122.9167 | 2.065 | 1.18
13 | 5.75 | 0 | 181.6277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 3.5205e-05 | 0.035205 | 100% | 83.3333 | 9.0625e-05 | 120.8333 | 2.03 | 1.16
13 | 5.875 | 0 | 181.4527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 3.5955e-05 | 0.035955 | 100% | 83.3333 | 8.9063e-05 | 118.75 | 1.995 | 1.14
13 | 6 | 0 | 181.2777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 3.6705e-05 | 0.036705 | 100% | 83.3333 | 8.75e-05 | 116.6667 | 1.96 | 1.12
13 | 6.125 | 0 | 181.1027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 3.7455e-05 | 0.037455 | 100% | 83.3333 | 8.5938e-05 | 114.5833 | 1.925 | 1.1
13 | 6.25 | 0 | 180.9277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 3.8205e-05 | 0.038205 | 100% | 83.3333 | 8.4375e-05 | 112.5 | 1.89 | 1.08
13 | 6.375 | 0 | 180.7527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 3.8955e-05 | 0.038955 | 100% | 83.3333 | 8.2813e-05 | 110.4167 | 1.855 | 1.06
13 | 6.5 | 0 | 180.5777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 3.9705e-05 | 0.039705 | 100% | 83.3333 | 8.125e-05 | 108.3333 | 1.82 | 1.04
13 | 6.625 | 0 | 180.4027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 4.0455e-05 | 0.040455 | 100% | 83.3333 | 7.9688e-05 | 106.25 | 1.785 | 1.02
13 | 6.75 | 0 | 180.2277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 4.1205e-05 | 0.041205 | 100% | 83.3333 | 7.8125e-05 | 104.1667 | 1.75 | 1
13 | 6.875 | 0 | 180.0527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 4.1955e-05 | 0.041955 | 100% | 83.3333 | 7.6562e-05 | 102.0833 | 1.715 | 0.98
13 | 7 | 0 | 179.8777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 4.2705e-05 | 0.042705 | 100% | 83.3333 | 7.5e-05 | 100 | 1.68 | 0.96
13 | 7.125 | 0 | 179.7027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 4.3455e-05 | 0.043455 | 100% | 83.3333 | 7.3438e-05 | 97.9167 | 1.645 | 0.94
13 | 7.25 | 0 | 179.5277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 4.4205e-05 | 0.044205 | 100% | 83.3333 | 7.1875e-05 | 95.8333 | 1.61 | 0.92
13 | 7.375 | 0 | 179.3527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 4.4955e-05 | 0.044955 | 100% | 83.3333 | 7.0313e-05 | 93.75 | 1.575 | 0.9
13 | 7.5 | 0 | 179.1777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 4.5705e-05 | 0.045705 | 100% | 83.3333 | 6.875e-05 | 91.6667 | 1.54 | 0.88
13 | 7.625 | 0 | 179.0027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 4.6455e-05 | 0.046455 | 100% | 83.3333 | 6.7188e-05 | 89.5833 | 1.505 | 0.86
13 | 7.75 | 0 | 178.8277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 4.7205e-05 | 0.047205 | 100% | 83.3333 | 6.5625e-05 | 87.5 | 1.47 | 0.84
13 | 7.875 | 0 | 178.6527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 4.7955e-05 | 0.047955 | 100% | 83.3333 | 6.4062e-05 | 85.4167 | 1.435 | 0.82
13 | 8 | 0 | 178.4777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 4.8705e-05 | 0.048705 | 100% | 83.3333 | 6.25e-05 | 83.3333 | 1.4 | 0.8
13 | 8.125 | 0 | 178.3027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 4.9455e-05 | 0.049455 | 100% | 83.3333 | 6.0938e-05 | 81.25 | 1.365 | 0.78
13 | 8.25 | 0 | 178.1277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 5.0205e-05 | 0.050205 | 100% | 83.3333 | 5.9375e-05 | 79.1667 | 1.33 | 0.76
13 | 8.375 | 0 | 177.9527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 5.0955e-05 | 0.050955 | 100% | 83.3333 | 5.7813e-05 | 77.0833 | 1.295 | 0.74
13 | 8.5 | 0 | 177.7777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 5.1705e-05 | 0.051705 | 100% | 83.3333 | 5.625e-05 | 75 | 1.26 | 0.72
13 | 8.625 | 0 | 177.6027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 5.2455e-05 | 0.052455 | 100% | 83.3333 | 5.4688e-05 | 72.9167 | 1.225 | 0.7
13 | 8.75 | 0 | 177.4277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 5.3205e-05 | 0.053205 | 100% | 83.3333 | 5.3125e-05 | 70.8333 | 1.19 | 0.68
13 | 8.875 | 0 | 177.2527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 5.3955e-05 | 0.053955 | 100% | 83.3333 | 5.1562e-05 | 68.75 | 1.155 | 0.66
13 | 9 | 0 | 177.0777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 5.4705e-05 | 0.054705 | 100% | 83.3333 | 5e-05 | 66.6667 | 1.12 | 0.64
13 | 9.125 | 0 | 176.9027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 5.5455e-05 | 0.055455 | 100% | 83.3333 | 4.8438e-05 | 64.5833 | 1.085 | 0.62
13 | 9.25 | 0 | 176.7277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 5.6205e-05 | 0.056205 | 100% | 83.3333 | 4.6875e-05 | 62.5 | 1.05 | 0.6
13 | 9.375 | 0 | 176.5527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 5.6955e-05 | 0.056955 | 100% | 83.3333 | 4.5313e-05 | 60.4167 | 1.015 | 0.58
13 | 9.5 | 0 | 176.3777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 5.7705e-05 | 0.057705 | 100% | 83.3333 | 4.375e-05 | 58.3333 | 0.98 | 0.56
13 | 9.625 | 0 | 176.2027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 5.8455e-05 | 0.058455 | 100% | 83.3333 | 4.2188e-05 | 56.25 | 0.945 | 0.54
13 | 9.75 | 0 | 176.0277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 5.9205e-05 | 0.059205 | 100% | 83.3333 | 4.0625e-05 | 54.1667 | 0.91 | 0.52
13 | 9.875 | 0 | 175.8527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 5.9955e-05 | 0.059955 | 100% | 83.3333 | 3.9063e-05 | 52.0833 | 0.875 | 0.5
13 | 10 | 0 | 175.6777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 6.0705e-05 | 0.060705 | 100% | 83.3333 | 3.75e-05 | 50 | 0.84 | 0.48
13 | 10.125 | 0 | 175.5027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 6.1455e-05 | 0.061455 | 100% | 83.3333 | 3.5937e-05 | 47.9167 | 0.805 | 0.46
13 | 10.25 | 0 | 175.3277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 6.2205e-05 | 0.062205 | 100% | 83.3333 | 3.4375e-05 | 45.8333 | 0.77 | 0.44
13 | 10.375 | 0 | 175.1527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 6.2955e-05 | 0.062955 | 100% | 83.3333 | 3.2813e-05 | 43.75 | 0.735 | 0.42
13 | 10.5 | 0 | 174.9777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 6.3705e-05 | 0.063705 | 100% | 83.3333 | 3.125e-05 | 41.6667 | 0.7 | 0.4
13 | 10.625 | 0 | 174.8027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 6.4455e-05 | 0.064455 | 100% | 83.3333 | 2.9687e-05 | 39.5833 | 0.665 | 0.38
13 | 10.75 | 0 | 174.6277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 6.5205e-05 | 0.065205 | 100% | 83.3333 | 2.8125e-05 | 37.5 | 0.63 | 0.36
13 | 10.875 | 0 | 174.4527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 6.5955e-05 | 0.065955 | 100% | 83.3333 | 2.6563e-05 | 35.4167 | 0.595 | 0.34
13 | 11 | 0 | 174.2777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 6.6705e-05 | 0.066705 | 100% | 83.3333 | 2.5e-05 | 33.3333 | 0.56 | 0.32
13 | 11.125 | 0 | 174.1027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 6.7455e-05 | 0.067455 | 100% | 83.3333 | 2.3438e-05 | 31.25 | 0.525 | 0.3
13 | 11.25 | 0 | 173.9277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 6.8205e-05 | 0.068205 | 100% | 83.3333 | 2.1875e-05 | 29.1667 | 0.49 | 0.28
13 | 11.375 | 0 | 173.7527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 6.8955e-05 | 0.068955 | 100% | 83.3333 | 2.0313e-05 | 27.0833 | 0.455 | 0.26
13 | 11.5 | 0 | 173.5777 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 6.9705e-05 | 0.069705 | 100% | 83.3333 | 1.875e-05 | 25 | 0.42 | 0.24
13 | 11.625 | 0 | 173.4027 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 7.0455e-05 | 0.070455 | 100% | 83.3333 | 1.7188e-05 | 22.9167 | 0.385 | 0.22
13 | 11.75 | 0 | 173.2277 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 7.1205e-05 | 0.071205 | 100% | 83.3333 | 1.5625e-05 | 20.8333 | 0.35 | 0.2
13 | 11.875 | 0 | 173.0527 | 16.6667 | 0.22 | 16.6667 | 16.6667 | 7.5e-07 | 7.1955e-05 | 0.071955 | 100% | 83.3333 | 1.4063e-05 | 18.75 | 0.315 | 0.18
13 | 12 | 6 | 172.8777 | 16.6667 | 6.22 | 16.6667 | 10.6667 | 1.1719e-06 | 7.3127e-05 | 0.073127 | 64% | 23.3333 | 1.9531e-05 | 16.6667 | 6.28 | 6.16
13 | 12.125 | 6 | 172.7027 | 16.6667 | 6.22 | 16.6667 | 10.6667 | 1.1719e-06 | 7.4299e-05 | 0.074299 | 64% | 23.3333 | 1.709e-05 | 14.5833 | 5.495 | 5.39
13 | 12.25 | 6 | 172.5277 | 16.6667 | 6.22 | 16.6667 | 10.6667 | 1.1719e-06 | 7.5471e-05 | 0.075471 | 64% | 23.3333 | 1.4648e-05 | 12.5 | 4.71 | 4.62
13 | 12.375 | 6 | 172.3527 | 16.6667 | 6.22 | 16.6667 | 10.6667 | 1.1719e-06 | 7.6643e-05 | 0.076643 | 64% | 23.3333 | 1.2207e-05 | 10.4167 | 3.925 | 3.85
13 | 12.5 | 6 | 172.1777 | 16.6667 | 6.22 | 16.6667 | 10.6667 | 1.1719e-06 | 7.7814e-05 | 0.077814 | 64% | 23.3333 | 9.7656e-06 | 8.3333 | 3.14 | 3.08
13 | 12.625 | 6 | 172.0027 | 16.6667 | 6.22 | 16.6667 | 10.6667 | 1.1719e-06 | 7.8986e-05 | 0.078986 | 64% | 23.3333 | 7.3242e-06 | 6.25 | 2.355 | 2.31
13 | 12.75 | 6 | 171.8277 | 16.6667 | 6.22 | 16.6667 | 10.6667 | 1.1719e-06 | 8.0158e-05 | 0.080158 | 64% | 23.3333 | 4.8828e-06 | 4.1667 | 1.57 | 1.54
13 | 12.875 | 6 | 171.6527 | 16.6667 | 6.22 | 16.6667 | 10.6667 | 1.1719e-06 | 8.133e-05 | 0.08133 | 64% | 23.3333 | 2.4414e-06 | 2.0833 | 0.785 | 0.77
13 | 13 | 6 | 171.4777 | 16.6667 | 6.22 | 16.6667 | 10.6667 | 1.1719e-06 | 8.2502e-05 | 0.082502 | 64% | 23.3333 | 0 | 0 | 0 | 0
[10 empty] | 0.5825 |  |  | 0 | 0

## SOA (hidden)
|  | Look Up |  |  |  |  | I = a * t^m
| 100us | 1ms | 10ms | 100ms | 1s/DC |  | a = iSOA1/tSOA1^m
Final SOA | 300 | 80 | 30 | 20 | 10 |  | m = log(iSOA1/iSOA2)/log(tSOA1/tSOA2)
| SOA Check - Based on Timer |  |  |  |  | SOA Predictor - dv/dt start-up
| time | 1.8889 | ms |  |  | time | 0.044288
| Voltage | 13 | V |  |  | Voltage | 13
| Lower time | 1 | ms |  |  | Lower time | 0.1
| Lower time (adjusted) | 1 |  |  |  | Lower time (adjusted) | 0.1
| Higher timer | 10 | ms |  |  | Higher time | 1
| Higher time (adjusted) | 10 |  |  |  | Higher time (adjusted) | 1
| I (lower time) | 80 | A |  |  | I (lower time) | 300
| I (higher time) | 30 | A |  |  | I (higher time) | 80
| Assuming Power vs time is linear on a log-log plot |  |  |  |  | Assuming Power vs time is linear on a log-log plot
| a | 80 |  |  |  | a | 80
| m | -0.42597 |  |  |  | m | -0.57403 | <-- Cannot plot zero on a log graph. If slope ~=0, then use 1e-12 as value
| Extr. I | 61.0147 | A |  |  | Extr. I | 478.8127
| Interpolated Power= | 793.1915 |  |  |  | Interpolated Power= | 6224.5657
[6 empty] | board hot? | Yes
| Derating factor = | 0.6662 |  |  |  | Temp for derating | 75.07
| Max Power with Temp Derating = | 528.4242 | W
[6 empty] | Derating factor = | 0.6662
[6 empty] | Max Power with Temp Derating = | 4146.8057
SOA Coefficients
|  | 0.1 to 1 ms | 1 to 10ms | 10ms to 100 ms | 100 ms to 1s
| t1 | 0.1 | 1 | 10 | 100
| t2 | 1 | 10 | 100 | 1000
| a | 80 | 80 | 45 | 80
| m | -0.57403 | -0.42597 | -0.17609 | -0.30103
MOSFET's SOA
| VDS | ID
| (V) | (A)
| 1 | 528.4242
| 1.2 | 440.3535
| 30 | 17.6141
Note on C39: Enter data from the MOSFET's SOA chart typically found in its datasheet. Consult the MOSFET vendor for SOA performance detail and appropriate derating criteria.
Note on C40: Enter data from the MOSFET's SOA chart typically found in its datasheet. Consult the MOSFET vendor for SOA performance detail and appropriate derating criteria.
Note on C41: Enter data from the MOSFET's SOA chart typically found in its datasheet. Consult the MOSFET vendor for SOA performance detail and appropriate derating criteria.

## dv_dt_recommendations (hidden)
Key Equations for SOA margin estimate:
1) Get total Energy = 1/2 CV^2 + E_load (t_worksheet) * t_start / t_ worksheet
note: t_worksheet is the start time from the start-up worksheet. E_load = Total Energy @ Start-up - 1/2CV^2
2) Get peak power: 4 Possible points with peak power
a) At Vin = 0 [mainly if there is no load or constant current load that starts at Vout = 0=
b) At Vin = Load start [ constant current=
c) When derivative of power = 0 [Peak, applies to resistive loads only=
P = (I_cap + Vout/R ) * (Vin - Vout) = Icap * Vin - Icap * Vout +Vin * Vout / R - Vout^2 / R
=> dP/dVout = -Icap + Vin/R -2Vout /R ; Zero when Vout = -R*I_cap / 2 + Vin / 2
Copied Inputs
| Temp_start_up | 75.07
| SOA margin target | 1.3 |  |  |  | SOA Coefficients
| Cap Energy (J) | 0.00845 |  |  |  |  | 0.1 to 1 ms | 1 to 10ms | 10ms to 100 ms | 100 ms to 1s
| E_load (t_worksheet) (J) | 0 |  |  |  | t1 | 0.1 | 1 | 10 | 100
| t_worksheet (ms) | 5.9091 |  |  |  | t2 | 1 | 10 | 100 | 1000
[6 empty] | a | 80 | 80 | 45 | 80
| Load Turn-On Threshold | 12 |  |  |  | m | -0.57403 | -0.42597 | -0.17609 | -0.30103
| Startup Load Type | Constant Current
| Startup Load Value | 6 |  |  |  | Initial | Final
|  |  |  | max slew rate |  | 12 | 13.6624
| Upper bound Slew Rate (4ms start-up) (V/ms) | 12 |  | min slew rate |  | 0.06 | 0.052699
| Min Slew Rate (400 ms start - up) (V/ms) | 0.06
| # of points | 20
| mult per point | 0.75665
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| slew rate (V/ms) | 12 | 9.0798 | 6.8702 | 5.1983 | 3.9333 | 2.9761 | 2.2519 | 1.7039 | 1.2892 | 0.97548 | 0.7381 | 0.55848 | 0.42257 | 0.31974 | 0.24193 | 0.18305 | 0.13851 | 0.1048 | 0.079297 | 0.06
| t_start (ms) | 1.0833 | 1.4318 | 1.8922 | 2.5008 | 3.3051 | 4.3681 | 5.773 | 7.6297 | 10.0836 | 13.3267 | 17.6129 | 23.2776 | 30.7641 | 40.6585 | 53.7351 | 71.0174 | 93.8581 | 124.0448 | 163.9401 | 216.6667
| I_cap (A) | 1.2 | 0.90798 | 0.68702 | 0.51983 | 0.39333 | 0.29761 | 0.22519 | 0.17039 | 0.12892 | 0.097548 | 0.07381 | 0.055848 | 0.042257 | 0.031974 | 0.024193 | 0.018305 | 0.013851 | 0.01048 | 0.0079297 | 0.006
| Total FET Energy (J) | 0.00845 | 0.00845 | 0.00845 | 0.00845 | 0.00845 | 0.00845 | 0.00845 | 0.00845 | 0.00845 | 0.00845 | 0.00845 | 0.00845 | 0.00845 | 0.00845 | 0.00845 | 0.00845 | 0.00845 | 0.00845 | 0.00845 | 0.00845
| Power (Vout= 0) , (W) | 15.6 | 11.8037 | 8.9312 | 6.7578 | 5.1133 | 3.8689 | 2.9274 | 2.215 | 1.676 | 1.2681 | 0.95952 | 0.72602 | 0.54934 | 0.41566 | 0.31451 | 0.23797 | 0.18006 | 0.13624 | 0.10309 | 0.078
| Power (load on), (W) | 7.2 | 6.908 | 6.687 | 6.5198 | 6.3933 | 6.2976 | 6.2252 | 6.1704 | 6.1289 | 6.0975 | 6.0738 | 6.0558 | 6.0423 | 6.032 | 6.0242 | 6.0183 | 6.0139 | 6.0105 | 6.0079 | 6.006
Vout (dP/dVout = 0) (V) | bar: 0.75665 1 to 0.75665 20
| Power (@ Vout above, if applicable) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| max power (W) | 15.6 | 11.8037 | 8.9312 | 6.7578 | 6.3933 | 6.2976 | 6.2252 | 6.1704 | 6.1289 | 6.0975 | 6.0738 | 6.0558 | 6.0423 | 6.032 | 6.0242 | 6.0183 | 6.0139 | 6.0105 | 6.0079 | 6.006
| Equivalent time for SOA (ms) | 0.54167 | 0.71588 | 0.94612 | 1.2504 | 1.3217 | 1.3418 | 1.3574 | 1.3694 | 1.3787 | 1.3858 | 1.3912 | 1.3953 | 1.3985 | 1.4009 | 1.4027 | 1.404 | 1.4051 | 1.4059 | 1.4065 | 1.4069
| a | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
| m | -0.57403 | -0.57403 | -0.57403 | -0.42597 | -0.42597 | -0.42597 | -0.42597 | -0.42597 | -0.42597 | -0.42597 | -0.42597 | -0.42597 | -0.42597 | -0.42597 | -0.42597 | -0.42597 | -0.42597 | -0.42597 | -0.42597 | -0.42597
| Available SOA (W) | 1478.6978 | 1259.9703 | 1073.5968 | 945.5662 | 923.4977 | 917.5827 | 913.0728 | 909.6403 | 907.0315 | 905.0508 | 903.5482 | 902.409 | 901.5458 | 900.8919 | 900.3967 | 900.0218 | 899.7379 | 899.5231 | 899.3605 | 899.2374
| Derated for Temp | 985.1085 | 839.3922 | 715.2302 | 629.9362 | 615.2342 | 611.2936 | 608.2891 | 606.0024 | 604.2644 | 602.9448 | 601.9438 | 601.1849 | 600.6098 | 600.1742 | 599.8443 | 599.5945 | 599.4054 | 599.2623 | 599.1539 | 599.072
| SOA Margin | 63.148 | 71.1127 | 80.082 | 93.2164 | 96.2307 | 97.0676 | 97.7142 | 98.2114 | 98.5923 | 98.8832 | 99.1048 | 99.2734 | 99.4016 | 99.4988 | 99.5726 | 99.6285 | 99.6708 | 99.7029 | 99.7272 | 99.7456
| Pass? | [20 empty] | N | bar: 0.75665 1 to 0.75665 20
| first yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2nd yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
| Mult 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| mult2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06