{"text_format":"1","workbook":"xlsx","n_sheets":5,"sheets":["LM(2)5118 Calculator","Bill of Materials","Bode Plots","Worksheet","Graph"],"not_rendered":{"charts":12,"images":1,"macros":0,"external_links":0,"defined_names":95,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"LM(2)5118 Calculator","index":0,"n_rows":113,"n_cols":7,"rows_kept":113,"cut":false,"hidden":false,"merged":[]}
["LM(2)5118 Quick Start Component Calculator",null,null,null,"Version 2.01"]
["Revision date:  April 2014"]
[]
[]
[]
[" Step 1 - Application Requirements"]
[null,null,"Vout (V)",null,12]
[" Enter design requirements in the shaded cells",null,"Vin(min) (V)",null,5]
[null,null,"Vin(max) (V)",null,42]
[null,null,"Maximum Average Load Current Iout (A)",null,3]
[null,null,"Ripple Current as % of Maximum Load Current (%)",null,0.4]
[null,null,"Effciency of Converter (%)",null,0.8]
[null,null,"VCCX Voltage (V)",null,0]
[null,null,"Vin at start of  Transition to Buck-Boost Mode (V)",null,{"$f":"1.33*Vout","v":15.96}]
[null,null,"Buck-Boost Mode Operation",null,{"$f":"IF(Vinmin<1.4*Vout,\"YES\",\"NO\")","v":"YES"}]
[]
[null,null,"Recommended Controller IC",null,{"$f":"IF(E15 = \"NO\", \"LM5116\", \"LM5118\")","v":"LM5118"}]
[]
["Step 2 - Switching Frequency"]
[null,null,"Maximum Possible Switching Frequency (kHz)",null,{"$f":"IF(Fmax<610,Fmax,500)","v":500}]
[{"$f":"IF(E21>=E20,\"Violation of Minimum On-Time or Max Frequency\",\"\")","v":""},null,"Switching Frequency (kHz)",null,300]
[{"$f":"IF(E21>=E20,\"Reduce Switching Frequency\",\"\")","v":""},null,"Timing Resistor, Rt (kW)",null,{"$f":"6.4*10^3/Fsw-3.02","v":18.313333333333333}]
[{"$f":"IF(Dviolate<DMaximumAll,\"Check Switching Frequency or Decrease Vin\",\"\")","v":""}]
["Step 3 - Inductor Value"]
[null,null,"Calculated Buck Mode Inductor Value, Lb (µH)",null,{"$f":"IF(Vinmax>E14,((Vout*(Vinmax-Vout))/(Vinmax*Fsw*(Ripple*Iout)))*1000,\"NA\")","v":23.809523809523807}]
[null,null,"Calculated Buck-Boost Mode Inductor Value, Lb-b (µH)",null,{"$f":"IF(BuckBoostMode=\"YES\",(((Vinmin)*Vout)/((Vinmin+Vout)*Fsw*Ripple*Iout))*1000,\"NA\")","v":9.8039215686274517}]
[null,null,"Actual Chosen Inductor Value, L (µH)",null,10]
[null,null,"Inductor Tolerance (%)",null,0.1]
[]
["Step 4 - Calculate Output and Inductor Currents Based on Chosen Inductor"]
[null,null,"Buck mode Ripple Current at Vin(max), ΔI (A)",null,{"$f":"IF(Vinmax>E14,((Vout*(Vinmax-Vout))/(Vinmax*L*Fsw))*1000,\"NA\")","v":2.8571428571428572}]
[null,null,"Buck-Boost Ripple Current at Vin(min), ΔI (A)",null,{"$f":"(Vout*Vinmin)/(Fsw*L*(Vout+Vinmin))*1000","v":1.1764705882352939}]
[null,null,"Buck-Boost Ripple Current at Vin=Vout, ΔI (A) ",null,{"$f":"IF(Vinmax>=Vout,(Vout*Vout)/((Vout+Vout)*Fsw*L)*1000,\"NA\")","v":2}]
[null,null,"Buck mode Ripple Current at Vin(max), Including inductor tolerance, ΔI (A)",null,{"$f":"IrippleBuck/(1-L_tol)","v":3.1746031746031744}]
[null,null,"Buck-Boost Ripple Current at Vin(min), Including inductor tolerance, ΔI (A)",null,{"$f":"IrippleBB/(1-L_tol)","v":1.3071895424836599}]
[null,null,"Buck Average Inductor Current at Vin(max), Including Effciency (A)",null,{"$f":"Iout/Eff","v":3.75}]
[null,null,"Buck-Boost Average Inductor Current at Vin(min), Including Effciency (A)",null,{"$f":"((Vout+Vinmin)/Vinmin)*(Iout/Eff)","v":12.75}]
[null,null,"Buck-Mode Peak Inductor Current, Ip(b) (A)",null,{"$f":"IF(Vinmax>E14,ILavgBuck+E34/2,\"NA\")","v":5.337301587301587}]
[null,null,"Buck-Boost Mode Peak Inductor Current, Ip(b-b) (A)",null,{"$f":"IF(BuckBoostMode=\"YES\",ILavgBB+E35/2,\"NA\")","v":13.40359477124183}," "]
[]
["Step 5 - Sense Resistor"]
[null,null,"Current Limit Margin (% beyond Max Load) (%)",null,0.2]
[null,null,"Buck Mode K Factor (K)",null,{"$f":"1+(10/(Vinmax-Vout))","v":1.3333333333333333}]
[null,null,"Selected Buck Mode K Factor (K)",null,1.1599999999999999]
[null,null,"Buck-Boost Mode K Factor (K)",null,{"$f":"1+(10/Vinmin)","v":3}]
[null,null,"Selected Buck-Boost Mode K Factor (K)",null,3]
[null,null,"Current Sense Resistor, Rs (mW)",null,{"$f":"IF((2.5*(1-E42))/(10*(ILavgBB+(IrippleBB*KBB)/2))*1000<(1.25*(1-E42))/(10*(ILavgBuck+(IrippleBuck*KBuck)/2))*1000,(2.5*(1-E42))/(10*(ILavgBB+(IrippleBB*KBB)/2))*1000,(1.25*(1-E42))/(10*(ILavgBuck+(IrippleBuck*KBuck)/2))*1000)","v":13.779128672745696}," "]
[null,null,"Closest Standard Value, Rs (mW)",null,15]
[]
["Step 6 - Ramp Capacitor"]
[null,null,"Cramp (pF)",null,{"$f":"(L*5*10^-6)/(10*Rs)*10^9","v":333.33333333333331}]
[null,null,"Closest Smaller Standard Value, Cramp (pF)",null,330]
[null,null,"Rramp (kW)",null,{"$f":"IF(Vout>20,7/(Vout*5*10^-6-50*10^-6)*10^-3,\"NA\")","v":"NA"}]
[]
["Step 7 - Current Limits"]
[null,null,"Buck Mode Peak Inductor Current Limit (A)",null,{"$f":"IF(ILPeakLimitBuck<IpeakBuck,\"Error\",ILPeakLimitBuck)","v":7.3713323713323708}]
[null,null,"Buck-Boost Mode Peak Inductor Current Limit (A)",null,{"$f":"IF(ILPeakLimitBB<IpeakBB,\"Error\",ILPeakLimitBB)","v":14.289958407605468}]
[]
["Step 9 - Output Capacitors (Based on Worst Case Conditions for Each Mode)"]
[null,null,"Target output ripple (mV)",null,50]
[null,null,"Buck-Boost Duty cycle at Vin(min) (%)",null,{"$f":"Vout/(Vinmin+Vout)","v":0.70588235294117652}]
[null,null,"Buck-Boost RMS Ripple Current in Output Cap (A)",null,{"$f":"SQRT(-(DBB*Iout^2)/(DBB-1))","v":4.6475800154489004}]
[null,null,"Minimum COUT output Capacitor Value (µF)",null,{"$f":"Iout*Vout/(Vinmin+Vout)/(Fsw*DeltaVout)*1000000","v":141.1764705882353}]
[null,null,"Required COUT ESR (mW)",null,{"$f":"DeltaVout/(Iout/(1-E61)+IrippleBB/2)","v":4.634678298800436}]
[null,null,"Chosen COUT output capacitor value (µF)",null,{"$f":"(47+280+0.47)*2","v":654.94000000000005}]
[null,null,"Actual COUT ESR (mW)",null,4.5999999999999996]
[null,null,"Buck Mode Output Ripple Voltage (mV)",null,{"$f":"IF(Vinmax<BuckMode,\"NA\",Coutesr*((Iout/(1-E61)+(IrippleBB/2))))","v":49.625882352941176}]
[]
["Step 10 - Input Capacitors (Based on Worst Case Conditions for Each Mode)"]
[null,null,"Buck-Boost RMS Input Ripple Current (A)",null,{"$f":"(Iout/(1-DBB))*SQRT(DBB*(1-DBB))","v":4.6475800154489004}]
[null,null,"Buck-Boost Mode Peak to Peak Current Ripple in Input Cap (A)",null,{"$f":"IpeakBB","v":13.40359477124183}]
[null,null,"Buck Mode RMS input Ripple Current (A)",null,{"$f":"IF(Vinmax<BuckMode,\"NA\",Iout*0.5)","v":1.5}]
[null,null,"Buck Mode Peak to Peak Current Ripple in Input Cap (A)",null,{"$f":"IpeakBuck","v":5.337301587301587}]
[null,null,"Initial Input Capacitor Value(μF)",null,{"$f":"E39/2/Fsw*1000","v":22.339324618736381}]
[null,null,"Chosen CIN Input Capacitor Value (µF)",null,{"$f":"2.2*5","v":11}]
[]
["Step 11 - Feedback Resistors"]
[null,null,"Rfb2 (W)",null,2670]
[null,null,"Rfb1 (W)",null,{"$f":"_Rfb2/((Vout/1.23)-1)","v":304.93036211699166}]
[]
["Step 12 - Chb & Cvcc Capacitor"]
[null,null,"High-side MOSFET Qg at VGS=10V (nC)",null,30]
[null,null,"Minimum Bootstrap Capacitor Chb (µF)",null,{"$f":"E82*10^-3/(0.05*7)","v":8.5714285714285701E-2}]
[null,null,"Chosen Value for Chb (µF)",null,0.1]
[null,null,"Minimum VCC Bypass Capacitor Cvcc (µF)",null,{"$f":"10*E84","v":1}]
[]
["Step 13 - Error Amplifier Compensation"]
[null,null,"Right Half Plane Zero Frequency (kHz)",null,{"$f":"((Rout*(1-DBB)^2)/(2*PI()*L*DBB*10^-6))/1000","v":7.8017128966615346}]
[null,null,"Capacitor ESR Zero Frequency (kHz)",null,{"$f":"1/(Cout*Coutesr*2*PI()*10^-6)","v":52.827588286180649}]
[null,null,"Capacitor Pole Frequency (kHz)",null,{"$f":"(1+DBB)/(2*PI()*Cout*Rout*10^-3)","v":0.10363529819671323}]
[null,null,"Bandwidth (kHz)",null,{"$f":"fmodRzero/4","v":1.9504282241653836}]
[null,null,"Selected Bandwith (kHz)",null,1.95]
[null,null,"Target Compensation Zero (kHz)",null,{"$f":"fcutoff/10","v":0.19500000000000001}]
[null,null,"Target Compensation Pole (kHz)",null,{"$f":"fmodRzero","v":7.8017128966615346}]
[null,null,"Cpole (nF)",null,{"$f":"fcompZero/(fcompPole*_Rfb2*CompGain)*10^9","v":1.8758445303963089}]
[null,null,"Select Nearest Standard Cpole Value (nF)",null,22]
[null,null,"Czero (nF)",null,{"$f":"((1/(CompGain*_Rfb2))-E95*10^-9)*10^9","v":73.174414264090274},null," "]
[null,null,"Select Nearest Standard Czero Value (nF)",null,100]
[null,null,"Rcomp (W)",null,{"$f":"1/(fcompZero*2*3.14*E97*10^-9)","v":11159.545060845228}]
[null,null,"Select nearest Standard Rcomp Value (W)",null,10000]
[]
["Step 14 - Soft Start capacitor"]
[null,null,"Choose soft-start time (ms)",null,12.3]
[null,null,"Soft Start Capacitor Value (nF)",null,{"$f":"(E103*10^(-5))/1.23*10^6","v":100}]
[]
["Step 15 - UVLO Threshold and Hiccup Mode Restart"]
[null,null,"Minimum Value of Resistor Ruv1  (kW)",null,{"$f":"Vinmax","v":42}]
[null,null,"Chosen Value of  Ruv1 (kW)",null,75]
[null,null,"Desired Undervoltage Threshold (V)",null,4]
[null,null,"Ruv2 Value (kW)",null,{"$f":"1.23*E108/(E109+5*E108*10^(-3)-1.23)","v":29.332273449920507}]
[null,null,"Choose off-time of hiccup duty cycle (µs)",null,723]
[null,null,"Vin voltage for desired hiccup mode off-time  (V)  ",null,12]
[null,null,"Hiccup Mode Off-time Capacitor Value Cr (nF)",null,{"$f":"-(E111*(E110+E108))/(E110*E108*LN(1-((0.98*(E110+E108))/(E110*E112))))","v":99.917863427169848}]

{"sheet":"Bill of Materials","index":1,"n_rows":21,"n_cols":5,"rows_kept":21,"cut":false,"hidden":false,"merged":[]}
[null,"LM5118 List of Components"]
[]
[null,"Component","Description","Value","Minimum Rating"]
[null,"L","Inductor",{"$f":"L","v":10},{"$f":"ILPeakLimitBB","v":14.289958407605468}]
[null,"Cin ","Input capacitor",{"$f":"Cin","v":11},{"$f":"Vinmax","v":42}]
[null,"Cramp","Ramp capacitor",{"$f":"Cramp","v":330},16]
[null,"Css","Soft start capacitor",{"$f":"Css","v":100},6]
[null,"Cout","Output capacitor",{"$f":"Cout","v":654.94000000000005},{"$f":"Vout","v":12}]
[null,"Cr","UVLO filter capacitor",{"$f":"Cr","v":99.917863427169848},16]
[null,"Cpole","Compensation capacitor",{"$f":"Cpole","v":22},6]
[null,"Czero","Compensation capacitor",{"$f":"Czero","v":100},6]
[null,"Cvcc","VCC bypass capacitor",{"$f":"Cvcc","v":1},12]
[null,"Chb","HB-SW bypass capacitor",{"$f":"Chb","v":0.1},{"$f":"MAX(Vccx,VCC)","v":7}]
[null,"Rfb1","Feedback resistor",{"$f":"_Rfb1","v":304.93036211699166},"1/16 W"]
[null,"Rfb2","Feedback resistor",{"$f":"_Rfb2","v":2670},"1/16 W"]
[null,"Ruv1","UVLO divider resistor",{"$f":"_Ruv1","v":75},{"$f":"IF(AND(Vinmax^2/(_Ruv2*1000)<0.05,Vinmax<=50),\"1/16W\",\"1/8W\")","v":"1/8W"}]
[null,"Ruv2","UVLO divider resistor",{"$f":"_Ruv2","v":29.332273449920507},"1/16 W"]
[null,"Rs","Sense resistor",{"$f":"Rs","v":15},{"$f":"IF(PRS_BB>PRS_B,PRS_BB,PRS_B)","v":2.4384375}]
[null,"Rt","Oscillator timing resistor",{"$f":"Rt","v":18.313333333333333},"1/16 W"]
[null,"Rramp","Optional ramp resistor",{"$f":"Rramp","v":"NA"},{"$f":"IF(D20=\"NA\",\"-\",\"1/16 W\")","v":"-"}]
[null,"Rcomp","Compensation resistor",{"$f":"Rcomp/1000","v":10},"1/16 W"]

{"sheet":"Bode Plots","index":2,"n_rows":24,"n_cols":24,"rows_kept":24,"cut":false,"hidden":false,"merged":[]}
["Buck-Boost Mode",null,null,null,null,null,null,null,null,null,null,null,"Buck Mode "]
[null,"Frequency (Hz)","Frequency (rad/sec)","Modulator\nGain\n(dB)","Modulator\nPhase\n(deg)","Error Amplifier Gain\n(dB)","Error Amplifier Phase (deg)","Overall Loop\nGain\n(dB)","Loop\nPhase\n(deg)",null,null,null,null,"Frequency (Hz)","Frequency (rad/sec)","Modulator\nGain\n(dB)","Modulator\nPhase\n(deg)","Error Amplifier Gain\n(dB)","Error Amplifier Phase (deg)","Overall Loop\nGain\n(dB)","Loop\nPhase\n(deg)"]
[null,0.1,{"$f":"2*PI()*B3","v":0.62831853071795862},{"$f":"20*LOG(AmBB*IMABS(IMDIV(IMPRODUCT(COMPLEX(1,-C3/wrBB),COMPLEX(1,C3/wzBB)),COMPLEX(1,C3/wpBB))))","v":13.2508107313111},{"$f":"IMARGUMENT(IMDIV(IMPRODUCT(COMPLEX(1,-C3/wrBB),COMPLEX(1,C3/wzBB)),COMPLEX(1,C3/wpBB)))*(180/PI())","v":-5.5911894432683205E-2},{"$f":"20*LOG(Afb*IMABS(IMDIV(IMDIV(COMPLEX(1,C3/wzea),COMPLEX(1,C3/wpea)),COMPLEX(0,C3))))","v":73.778982450823577},{"$f":"IMARGUMENT(IMDIV(IMDIV(COMPLEX(-1,-C3/wzea),COMPLEX(1,C3/wpea)),COMPLEX(0,C3)))*(180/PI())","v":90.029508192011676},{"$f":"D3+F3","v":87.029793182134682},{"$f":"E3+G3","v":89.973596297578993},null,"Modulator - Buck-Boost",null,null,0.1,{"$f":"2*PI()*N3","v":0.62831853071795862},{"$f":"20*LOG(Amb*IMABS(IMDIV(COMPLEX(1,O3/wzb),COMPLEX(1,O3/wpb))))","v":28.519362878441687},{"$f":"IMARGUMENT(IMDIV(COMPLEX(1,O3/wzb),COMPLEX(1,O3/wpb)))*(180/PI())","v":-9.4202816758518271E-2},{"$f":"20*LOG(Afb*IMABS(IMDIV(IMDIV(COMPLEX(1,O3/wzea),COMPLEX(1,O3/wpea)),COMPLEX(0,O3))))","v":73.778982450823577},{"$f":"IMARGUMENT(IMDIV(IMDIV(COMPLEX(-1,-O3/wzea),COMPLEX(1,O3/wpea)),COMPLEX(0,O3)))*(180/PI())","v":90.029508192011676},{"$f":"P3+R3","v":102.29834532926526},{"$f":"Q3+S3","v":89.935305375253151},null,"Modulator - Buck"]
[null,0.2,{"$f":"2*PI()*B4","v":1.2566370614359172},13.250798602706437,-0.11182368591466146,67.758387513857016,90.059016355765607,81.009186116563455,89.947192669850949,null,"rad/sec","Hz",null,0.2,{"$f":"2*PI()*N4","v":1.2566370614359172},28.519327577621155,-0.18840512245546898,67.758387513857016,90.059016355765607,{"$f":"P4+R4","v":96.277715091478171},{"$f":"Q4+S4","v":89.870611233310143},null,"rad/sec","Hz"]
[null,0.5,{"$f":"2*PI()*B5","v":3.1415926535897931},13.250713703422594,-0.27955741317346799,59.799622174437047,90.147540394906272,73.050335877859638,89.867982981732808,"wp",{"$f":"(1+DBB)/(Cout*10^-6*Rout)","v":651.15978293476371},{"$f":"K5/(2*PI())","v":103.63529819671324},null,0.5,{"$f":"2*PI()*N5","v":3.1415926535897931},28.519080479911345,-0.47100386291016555,59.799622174437047,90.147540394906272,88.318702654348385,89.676536531996106,"wz",{"$f":"1/(Cout*10^-6*Coutesr*10^-3)","v":331925.52653346269},{"$f":"W5/(2*PI())","v":52827.588286180653}]
[null,1,{"$f":"2*PI()*B6","v":6.2831853071795862},13.250410505247114,-0.55910195837142462,53.779146665940416,90.295077257695027,67.029557171187534,89.735975299323599,"wr",{"$f":"(Rout*(1-DBB)^2)/(L*10^-6*DBB)","v":49019.607843137244},{"$f":"K6/(2*PI())","v":7801.7128966615346},null,1,{"$f":"2*PI()*N6","v":6.2831853071795862},28.518198102840188,-0.94194385558415317,53.779146665940416,90.295077257695027,82.297344768780604,89.353133402110871,"wp",{"$f":"1/(Cout*10^-6*Rout)","v":381.71435551348213},{"$f":"W6/(2*PI())","v":60.751726529107756}]
[null,2,{"$f":"2*PI()*B7","v":12.566370614359172},13.249197924251693,-1.1181009944985676,47.7590443337645,90.590126260973733,61.008242258016196,89.472025266475171,"wz",{"$f":"1/(Cout*10^-6*Coutesr*10^-3)","v":331925.52653346269},{"$f":"K7/(2*PI())","v":52827.588286180653},null,2,{"$f":"2*PI()*N7","v":12.566370614359172},28.514670386236443,-1.8833770605228404,47.7590443337645,90.590126260973733,76.273714720000939,88.706749200450886,null,"Gain","dB"]
[null,5,31.415926535897931,13.240719327197057,-2.7934537577034382,39.803725525492915,91.474821482638689,53.044444852689971,88.681367724935257,null,"Gain","dB",null,5,31.415926535897931,28.490056280324044,-4.6995409582504912,39.803725525492915,91.474821482638689,68.293781805816963,86.775280524388194,"Am",{"$f":"Rout/Ri","v":26.666666666666668},{"$f":"20*LOG(Amb)","v":28.519374645445623}]
[null,10,62.831853071795862,13.210573082526157,-5.5741278822846132,33.795534800245029,92.946121229686497,47.00610788277119,87.371993347401883,"Am",{"$f":"(Rout/Ri)*((1-DBB)/(1+DBB))","v":4.5977011494252862},{"$f":"20*LOG(K9)","v":13.250814774186875},null,10,62.831853071795862,28.403270340355277,-9.3364710392396653,33.795534800245029,92.946121229686497,62.198805140600307,83.609650190446828]
[null,20,125.66370614359172,13.092038835771794,-11.048102378963701,27.824196498902843,95.8643173211549,40.916235334674639,84.816214942191195,null,null,null,null,20,125.66370614359172,28.072494724697584,-18.200305635685854,27.824196498902843,95.8643173211549,55.896691223600428,77.664011685469049]
[null,50,314.15926535897933,12.342181002213877,-26.068467243610129,20.19444033397324,104.19815865803666,32.536621336187117,78.129691414426532,null,"Error Amp",null,null,50,314.15926535897933,26.273102742294011,-39.400898672814229,20.19444033397324,104.19815865803666,46.467543076267248,64.797259985222439,null,"Error Amp"]
[null,100,628.31853071795865,10.393552710097103,-44.603165991911155,15.168652551078114,115.67767214957608,25.562205261175215,71.074506157664928,null,"rad/sec","Hz",null,100,628.31853071795865,22.826283236861808,-58.612138814892674,15.168652551078114,115.67767214957608,37.994935787939923,57.065533334683408,null,"rad/sec","Hz"]
[null,200,1256.6370614359173,6.5103560102578353,-63.85943434888555,11.655648876112723,128.72013907594339,18.166004886370558,64.860704727057851,"wpea",{"$f":"(Czero*10^-9+Cpole*10^-9)/(Cpole*10^-9*Czero*10^-9*Rcomp)","v":5545.454545454545},{"$f":"wpea/(2*PI())","v":882.58650260051047},null,200,1256.6370614359173,17.786712176031326,-72.886473347612537,11.655648876112723,128.72013907594339,29.442361052144051,55.833665728330857,"wpea",{"$f":"(Czero*10^-9+Cpole*10^-9)/(Cpole*10^-9*Czero*10^-9*Rcomp)","v":5545.454545454545},{"$f":"wpea/(2*PI())","v":882.58650260051047}]
[null,500,3141.5926535897929,-0.5829219670017618,-81.414791746717952,8.9528832920970061,132.81093462179754,8.3699613250952449,51.39614287507959,"wzea",{"$f":"1/(Czero*10^-9*Rcomp)","v":1000},{"$f":"wzea/(2*PI())","v":159.15494309189535},null,500,3141.5926535897929,10.147889467296686,-82.530048936234266,8.9528832920970061,132.81093462179754,19.100772759393692,50.280885685563277,"wzea",{"$f":"1/(Czero*10^-9*Rcomp)","v":1000},{"$f":"wzea/(2*PI())","v":159.15494309189535}]
[null,1000,6283.1853071795858,-6.4130990802812473,-90.302978683827661,6.2647024581390651,122.38812784195335,-0.14839662214218219,32.085149158125688,null,"Gain","dB",null,1000,6283.1853071795858,4.1761037404855035,-85.439004191957039,6.2647024581390651,122.38812784195335,10.440806198624568,36.949123649996309,null,"Gain","dB"]
[null,2000,12566.370614359172,-12.188635910201713,-99.243962595132658,1.8918061084552269,109.2616788689153,-10.296829801746487,10.017716273782639,"Afb",{"$f":"1/(_Rfb2*(Czero*10^-9+Cpole*10^-9))","v":3069.9330754589546},{"$f":"20*LOG(K16)","v":69.742578159213537},null,2000,12566.370614359172,-1.8278378234254513,-86.092000413198164,1.8918061084552269,109.2616788689153,6.3968285029775585E-2,23.169678455717133,"Afb",{"$f":"1/(_Rfb2*(Czero*10^-9+Cpole*10^-9))","v":3069.9330754589546},{"$f":"20*LOG(W16)","v":69.742578159213537}]
[null,5000,31415.926535897932,-18.887115462816865,-116.06099742342374,-5.4505318624197496,98.18740964526738,-24.337647325236617,-17.873587778156363,null,null,null,null,5000,31415.926535897932,-9.7507625125749158,-83.897074131012857,-5.4505318624197496,98.18740964526738,-15.201294374994665,14.290335514254522]
[null,10000,62831.853071795864,-22.06573893317546,-130.72692486185619,-11.374874946427253,94.131965267136366,-33.440613879602715,-36.594959594719825,null,null,null,null,10000,62831.853071795864,-15.656717353745439,-78.932944847078858,-11.374874946427253,94.131965267136366,-27.03159230017269,15.199020420057508]
[null,20000,125663.70614359173,-23.086075837701575,-137.65689885498713,-17.371050327542882,92.070849013278718,-40.45712616524446,-45.586049841708416,null,null,null,null,20000,125663.70614359173,-21.248375194606854,-69.089791865558155,-17.371050327542882,92.070849013278718,-38.61942552214974,22.981057147720563]
[null,50000,314159.26535897929,-21.400419388969713,-127.58779268448868,-25.322985274105779,90.828887096061749,-46.723404663075492,-36.758905588426927,null,null,null,null,50000,314159.26535897929,-27.010899287115862,-46.505525738459212,-25.322985274105779,90.828887096061749,-52.333884561221637,44.323361357602536]
[null,100000,628318.53071795858,-17.644735385091465,-113.32601885445374,-31.342603494495734,90.414482698615629,-48.987338879587199,-22.911536155838107,null,null,null,null,100000,628318.53071795858,-29.197708657942961,-27.811605263426451,-31.342603494495734,90.414482698615629,-60.540312152438695,62.602877435189178]
[null,200000,1256637.0614359172,-12.419944441573794,-102.53248306367141,-37.362957947544743,90.207246243993481,-49.782902389118533,-12.325236819677926,null,null,null,null,200000,1256637.0614359172,-29.97376946201037,-14.778661787566925,-37.362957947544743,90.207246243993481,-67.33672740955511,75.428584456426563]
[null,500000,3141592.653589793,-4.7113772704374854,-95.125406286628404,-45.321689389467636,90.08289904582692,-50.033066659905124,-5.0425072408014842,null,null,null,null,500000,3141592.653589793,-30.218456844131737,-6.0242582823436859,-45.321689389467636,90.08289904582692,-75.540146233599373,84.05864076348324]
[null,1000000,6283185.307179586,1.2723213237818054,-92.571052854971924,-51.34227948386421,90.04144956207314,-50.069958160082408,-2.5296032928987842,null,null,null,null,1000000,6283185.307179586,-30.254565353217544,-3.0205060556567882,-51.34227948386421,90.04144956207314,-81.596844837081761,87.020943506416359]

{"sheet":"Worksheet","index":3,"n_rows":89,"n_cols":6,"rows_kept":89,"cut":false,"hidden":true,"merged":[]}
[]
[null,null,null,null,"10 is buck","10 is buck-boost"]
[]
[null,{"$f":"IF(Vout>0.7*Vin_nominal,\"Buck-Boost Mode\",\"Buck Mode\")","v":{"$error":"#NAME?"}},null,"Vin","Vout"]
[null,null,null,null,12]
[null,null,null,20,{"$f":"IF(E5<0.7*D6,10,0)","v":10},{"$f":"IF(E5>0.7*D6,10,0)","v":0}]
[null,null,null,19,{"$f":"IF(E5<0.7*D7,10,0)","v":10},{"$f":"IF(E5>0.7*D7,10,0)","v":0}]
[null,null,null,18,{"$f":"IF(E5<0.7*D8,10,0)","v":10},{"$f":"IF(E5>0.7*D8,10,0)","v":0}]
[null,null,null,17,{"$f":"IF(E5<0.7*D9,10,0)","v":0},{"$f":"IF(E5>0.7*D9,10,0)","v":10}]
[null,null,null,16,{"$f":"IF(E5<0.7*D10,10,0)","v":0},{"$f":"IF(E5>0.7*D10,10,0)","v":10}]
[null,null,null,14,{"$f":"IF(E7<0.7*D11,10,0)","v":0},{"$f":"IF(E5>0.7*D11,10,0)","v":10}]
[null,null,null,13,{"$f":"IF(E8<0.7*D12,10,0)","v":0},{"$f":"IF(E5>0.7*D12,10,0)","v":10}]
[null,null,null,12,{"$f":"IF(E5<0.7*D13,10,0)","v":0},{"$f":"IF(E5>0.7*D13,10,0)","v":10}]
[null,null,null,11,{"$f":"IF(E5<0.7*D14,10,0)","v":0},{"$f":"IF(E5>0.7*D14,10,0)","v":10}]
[null,null,null,10,{"$f":"IF(E5<0.7*D15,10,0)","v":0},{"$f":"IF(E5>0.7*D15,10,0)","v":10}]
[]
[null,null,null,null,12]
[null,null,13,75,{"$f":"E17/0.7","v":17.142857142857142},{"$f":"E18","v":17.142857142857142}]
[null,null,13,74,{"$f":"E17/0.7","v":17.142857142857142}]
[null,null,13,73,{"$f":"E17/0.7","v":17.142857142857142}]
[null,null,13,72,{"$f":"E17/0.7","v":17.142857142857142}]
[null,null,13,71,{"$f":"E17/0.7","v":17.142857142857142}]
[null,null,13,70,{"$f":"E17/0.7","v":17.142857142857142}]
[null,null,13,{"$f":"D23-1","v":69},{"$f":"E17/0.7","v":17.142857142857142}]
[null,null,13,68,{"$f":"E17/0.7","v":17.142857142857142}]
[null,null,13,67,{"$f":"E17/0.7","v":17.142857142857142}]
[null,null,13,66,{"$f":"E17/0.7","v":17.142857142857142}]
[null,null,13,65,{"$f":"E17/0.7","v":17.142857142857142}]
[null,null,13,64,17.142857142857142]
[null,null,13,63,17.142857142857142]
[null,null,13,62,17.142857142857142]
[null,null,13,61,17.142857142857142]
[null,null,13,60,17.142857142857142]
[null,null,13,{"$f":"D33-1","v":59},17.142857142857142]
[null,null,13,58,17.142857142857142]
[null,null,13,57,17.142857142857142]
[null,null,13,56,17.142857142857142]
[null,null,13,55,17.142857142857142]
[null,null,13,54,17.142857142857142]
[null,null,13,53,17.142857142857142]
[null,null,13,52,17.142857142857142]
[null,null,13,51,17.142857142857142]
[null,null,13,50,17.142857142857142]
[null,null,13,49,17.142857142857142]
[null,null,13,48,17.142857142857142]
[null,null,13,47,17.142857142857142]
[null,null,13,46,17.142857142857142]
[null,null,13,45,17.142857142857142]
[null,null,13,44,17.142857142857142]
[null,null,13,43,17.142857142857142]
[null,null,13,42,17.142857142857142]
[null,null,13,41,17.142857142857142]
[null,null,13,40,17.142857142857142]
[null,null,13,39,17.142857142857142]
[null,null,13,38,17.142857142857142]
[null,null,13,37,17.142857142857142]
[null,null,13,36,17.142857142857142]
[null,null,13,35,17.142857142857142]
[null,null,13,34,17.142857142857142]
[null,null,13,33,17.142857142857142]
[null,null,13,32,17.142857142857142]
[null,null,13,31,17.142857142857142]
[null,null,13,30,17.142857142857142]
[null,null,13,29,17.142857142857142]
[null,null,13,28,17.142857142857142]
[null,null,13,27,17.142857142857142]
[null,null,13,26,17.142857142857142]
[null,null,13,25,17.142857142857142]
[null,null,13,24,17.142857142857142]
[null,null,13,23,17.142857142857142]
[null,null,13,22,17.142857142857142]
[null,null,13,21,17.142857142857142]
[null,null,13,20,17.142857142857142]
[null,null,13,19,17.142857142857142]
[null,null,13,18,17.142857142857142]
[null,null,13,17,17.142857142857142]
[null,null,13,16,17.142857142857142]
[null,null,13,15,17.142857142857142]
[null,null,13,14,17.142857142857142]
[null,null,13,13,17.142857142857142]
[null,null,13,12,17.142857142857142]
[null,null,13,11,17.142857142857142]
[null,null,13,10,17.142857142857142]
[null,null,13,9,17.142857142857142]
[null,null,13,8,17.142857142857142]
[null,null,13,7,17.142857142857142]
[null,null,13,6,17.142857142857142]
[null,null,13,5,17.142857142857142]
[null,null,13,4,17.142857142857142]

{"sheet":"Graph","index":4,"n_rows":13,"n_cols":13,"rows_kept":13,"cut":false,"hidden":true,"merged":[]}
[]
[]
[]
[null,null,"Vinmin","Vinmax","Lower ts limit","Upper ts limit","Lo B-B Voltage","Hi B-B voltage","Lower Buck","Upper Buck"]
[]
[]
[null,null,{"$f":"Vinmin","v":5},{"$f":"Vinmax","v":42},{"$f":"1.15*Vout","v":13.799999999999999},{"$f":"Vout/0.75","v":16},{"$f":"Vinmin","v":5},{"$f":"E7","v":13.799999999999999},{"$f":"Vout/0.75","v":16},{"$f":"Vinmax","v":42},null,{"$f":"Vout","v":12},{"$f":"Vin_nominal","v":{"$error":"#NAME?"}}]
[null,null,"Buck-Boost",null,null,null,5,{"$f":"IF(Vinmax<H7,Vinmax,H7)","v":13.799999999999999}]
[null,null,"Graph-Trans",null,null,{"$f":"IF(Vinmax>F7,F7,IF(Vinmax>E7,Vinmax,0))","v":16}]
[null,null,"Offset-Trans",null,null,{"$f":"F9-H8","v":2.2000000000000011}]
[]
[null,"NEW ","Buck",null,null,null,null,{"$f":"IF(Vinmax>F7,Vinmax,0)","v":42}]
[null,"Offset","Offset-Buck",null,null,null,null,{"$f":"H12-F7","v":26}]