## 回答(キャリブレーション)
OUTPUT CURRENT(mA)
Target current[mA] | Sample1 CAL_OFF | Sample1 CAL_ON | Sample1 Δ[mA] |  | Sample2 CAL_OFF | Sample2 CAL_ON | Sample2 Δ[mA] |  | Sample3 CAL_OFF | Sample3 CAL_ON | Sample3 Δ[mA] | Sample4 CAL_OFF | Sample4 CAL_ON | Sample4 Δ[mA] | DAC_DATA
4 | 3.9856 | 4.0011 | -0.0011 |  | 3.9833 | 4.0011 | -0.0011 |  | 3.9903 | 4.0009 | -0.0009 | 3.9843 | 4.0006 | -0.0006 | 0
5 | 4.982 | 4.997 | 0.003 |  | 4.9783 | 4.9963 | 0.0037 |  | 4.9882 | 4.999 | 0.001 | 4.9801 | 4.9969 | 0.0031 | 1000
6 | 5.9784 | 5.9942 | 0.0058 |  | 5.9745 | 5.9925 | 0.0075 |  | 5.9847 | 5.9959 | 0.0041 | 5.9764 | 5.9937 | 0.0063 | 2000
7 | 6.9744 | 6.9909 | 0.0091 |  | 6.9705 | 6.9891 | 0.0109 |  | 6.9813 | 6.993 | 0.007 | 6.9729 | 6.9904 | 0.0096 | 3000
8 | 7.9699 | 7.9869 | 0.0131 |  | 7.9657 | 7.9847 | 0.0153 |  | 7.9798 | 7.9917 | 0.0083 | 7.9692 | 7.987 | 0.013 | 4000
9 | 8.9657 | 8.983 | 0.017 |  | 8.9607 | 8.9801 | 0.0199 |  | 8.9777 | 8.9899 | 0.0101 | 8.9651 | 8.9834 | 0.0166 | 5000
10 | 9.9623 | 9.9803 | 0.0197 |  | 9.9565 | 9.9765 | 0.0235 |  | 9.9742 | 9.9865 | 0.0135 | 9.9618 | 9.9803 | 0.0197 | 6000
11 | 10.9592 | 10.9773 | 0.0227 |  | 10.9527 | 10.9732 | 0.0268 |  | 10.971 | 10.9837 | 0.0163 | 10.9582 | 10.977 | 0.023 | 7000
12 | 11.9547 | 11.9732 | 0.0268 |  | 11.948 | 11.9689 | 0.0311 |  | 11.9691 | 11.9819 | 0.0181 | 11.9543 | 11.9736 | 0.0264 | 8000
13 | 12.9502 | 12.969 | 0.031 |  | 12.9432 | 12.9642 | 0.0358 |  | 12.9672 | 12.9801 | 0.0199 | 12.9504 | 12.97 | 0.03 | 9000
14 | 13.9464 | 13.9655 | 0.0345 |  | 13.939 | 13.9605 | 0.0395 |  | 13.9636 | 13.9768 | 0.0232 | 13.9467 | 13.9667 | 0.0333 | A000
15 | 14.943 | 14.9622 | 0.0378 |  | 14.935 | 14.9567 | 0.0433 |  | 14.962 | 14.9734 | 0.0266 | 14.9432 | 14.9632 | 0.0368 | B000
16 | 15.9387 | 15.9583 | 0.0417 |  | 15.93 | 15.9522 | 0.0478 |  | 15.958 | 15.9715 | 0.0285 | 15.9391 | 15.9597 | 0.0403 | C000
17 | 16.9342 | 16.9541 | 0.0459 |  | 16.9253 | 16.9478 | 0.0522 |  | 16.9562 | 16.97 | 0.03 | 16.9352 | 16.956 | 0.044 | D000
18 | 17.9307 | 17.9509 | 0.0491 |  | 17.9214 | 17.9441 | 0.0559 |  | 17.9529 | 17.9668 | 0.0332 | 17.9319 | 17.953 | 0.047 | E000
19 | 18.9273 | 18.9477 | 0.0523 |  | 18.9173 | 18.9406 | 0.0594 |  | 18.9494 | 18.9638 | 0.0362 | 18.9282 | 18.9495 | 0.0505 | F000
20 | 19.923 | 19.9243 | 0.0757 |  | 19.9123 | 19.9136 | 0.0864 |  | 19.9475 | 19.9485 | 0.0515 | 19.924 | 19.9254 | 0.0746 | FFFF
CAL_ON/CAL_OFF : Calibration ON/OFF
キャリブレーション補正値は下記
Accracy[％FSR]
Target current [mA] | 199_CH1_CALOFF | 199_CH1_CALON | 199_CH2_CALOFF | 199_CH2_CALON | 200_CH1_CALOFF | 200_CH1_CALON | 200_CH2_CALOFF | 200_CH1_CALON | DAC_DATA
4 | -0.09 | 0.006875 | -0.10438 | 0.006875 | -0.060625 | 0.005625 | -0.098125 | 0.00375 | 0
5 | -0.1125 | -0.01875 | -0.13562 | -0.023125 | -0.07375 | -0.00625 | -0.12437 | -0.019375 | 1000
6 | -0.135 | -0.03625 | -0.15938 | -0.046875 | -0.095625 | -0.025625 | -0.1475 | -0.039375 | 2000
7 | -0.16 | -0.056875 | -0.18437 | -0.068125 | -0.11688 | -0.04375 | -0.16937 | -0.06 | 3000
8 | -0.18812 | -0.081875 | -0.21438 | -0.095625 | -0.12625 | -0.051875 | -0.1925 | -0.08125 | 4000
9 | -0.21438 | -0.10625 | -0.24563 | -0.12437 | -0.13937 | -0.063125 | -0.21813 | -0.10375 | 5000
10 | -0.23562 | -0.12313 | -0.27187 | -0.14688 | -0.16125 | -0.084375 | -0.23875 | -0.12313 | 6000
11 | -0.255 | -0.14188 | -0.29562 | -0.1675 | -0.18125 | -0.10187 | -0.26125 | -0.14375 | 7000
12 | -0.28312 | -0.1675 | -0.325 | -0.19438 | -0.19313 | -0.11313 | -0.28563 | -0.165 | 8000
13 | -0.31125 | -0.19375 | -0.355 | -0.22375 | -0.205 | -0.12437 | -0.31 | -0.1875 | 9000
14 | -0.335 | -0.21562 | -0.38125 | -0.24688 | -0.2275 | -0.145 | -0.33313 | -0.20813 | A000
15 | -0.35625 | -0.23625 | -0.40625 | -0.27063 | -0.2375 | -0.16625 | -0.355 | -0.23 | B000
16 | -0.38312 | -0.26063 | -0.4375 | -0.29875 | -0.2625 | -0.17812 | -0.38063 | -0.25188 | C000
17 | -0.41125 | -0.28687 | -0.46687 | -0.32625 | -0.27375 | -0.1875 | -0.405 | -0.275 | D000
18 | -0.43312 | -0.30687 | -0.49125 | -0.34938 | -0.29438 | -0.2075 | -0.42563 | -0.29375 | E000
19 | -0.45438 | -0.32687 | -0.51687 | -0.37125 | -0.31625 | -0.22625 | -0.44875 | -0.31562 | F000
20 | -0.48125 | -0.47313 | -0.54813 | -0.54 | -0.32812 | -0.32188 | -0.475 | -0.46625 | FFFF
FFFF
Current output value after calibration
No. | OFFSETerr IOUT4mA-4 | Error(/1LSB) OFFSETerr/q | Calibrated OFFSET value (DEC) | Calibrated OFFSET value (HEX) | @16mA (IOUT20mA-4) | @16mA-OFFSETerr | Gain error GAINerr | Gain error [/1LSB] GAINErr/q | Calibrated GAIN value(DEC) | Calibrated GAIN value(HEX)
Sample1 | -0.0157 | -64.3062 | 64 | 40 | 15.918 | 15.9337 | 0.0041438 | 16.9725 | 32785 | 8011
Sample2 | -0.0179 | -73.3173 | 73 | 49 | 15.9075 | 15.9254 | 0.0046625 | 19.0973 | 32787 | 8013
Sample3 | -0.0111 | -45.4649 | 45 | 2D | 15.943 | 15.9541 | 0.0028687 | 11.7502 | 32780 | 800C
Sample4 | -0.0166 | -67.9926 | 68 | 44 | 15.9187 | 15.9353 | 0.0040437 | 16.5629 | 32785 | 8011
| OFFSETerr＝IOUT4mA-4 |  |  |  | OFFSET ERROR
| OFFSET=-OFFSETerr/q |  |  |  | OFFSET error after calibration (integer value)
| IOUT4mA |  |  |  | Current output value@4mA(DAC_DATA=0x0000)
| q=16/65535＝ |  |  |  | 0.00024414
| GAINerr=1-(IOUT20mA-4-OFFSETerr)/16 |  |  |  | GAIN ERROR
| GAIN=32768+GAINerr/q |  |  |  | GAIN error after calibration(integer value)
| IOUT20mA |  |  |  | Current output value@20mA(DAC_DATA=0xFFFF)
※Calibration calculations used the following measured values.
Measured value
| Voltage |  |  |  | Current
| Sample1_0V[V] | Sample2_0V[V] | Sample1_10V[V] | Sample2_10V[V] | Sample1_4mA[mA] | Sample2_4mA[mA] | Sample1_20mA[mA] | sample2_20mA[mA]
| 0.0003 | -0.0005 | 9.9951 | 9.9936 | 3.9843 | 3.9821 | 19.918 | 19.9075
| Sample3_0V[V] | Sample4_0V[V] | Sample3_10V[V] | Sample4_10V[V] | Sample3_4mA[mA] | Sample4_4mA[mA] | Sample3_20mA[mA] | sample4_20mA[mA]
| -0.0003 | 0.0004 | 9.995 | 9.9937 | 3.9889 | 3.9834 | 19.943 | 19.9187
sample1
sample2
sample1
sample2
sample3
sample3
sample4
sample4